## SUMMARY
PUBLIC PROCUREMENT CONTRACT FOR SUPPLY AND INSTALLATION OF ROOF-TOP SOLAR PHOTOVOLTAIC SYSTEMS ON SCHOOLS IN GAZA STRIP
TENDER NO. PZA1203211-10026
ANNEX 1 – BILL OF QUANTITIES
SUMMARY SHEET
Lot no. |  | Total (EUR)
LOT 1 - Five schools with 41.6 KW PV modules |  | 0
LOT 2 - Five schools with 39 KW PV modules |  | 0
Grand Total [Excluding VAT] |  | 0
Total to be reported by tenderers in Tender Documents cf. 3.3 Form 3: Prices, p.42 of 57
Name of Tenderer (Company)
Authorized person to sign
In the Capacity of
| Date | 2023-05-15
| Time | 45061.5538
Signature
Stamp

## LOT 1 - BOQ
PUBLIC PROCUREMENT CONTRACT FOR SUPPLY AND INSTALLATION OF ROOF-TOP SOLAR PHOTOVOLTAIC SYSTEMS ON SCHOOLS IN GAZA STRIP
TENDER NO. PZA1203211-10026
ANNEX 1 – BILL OF QUANTITIES
LOT 1 - FIVE SCHOOLS WITH 41.6 KW PV MODULES
FAHMI EL GERGAWI HIGH SCHOOL, AL BORAGE HIGH SCHOOL, HAMAD BEN KHALEFA HIGH SCHOOL, EL MANFALOTY HIGH SCHOOL, AHMED EL SHOQERI HIGH SCHOOL
1 | PV Modules: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
1.1 | Supply, install, connect, and operate BIFACIAL MONO PV Solar Modules (Min total arrays capacity not less 41.6KWp for each school). The item includes the supply, installation, and connection of the following: | KWp | 208 |  | 0
· PVC ducts with clamps, accessories, supports & labels suitable to be installed under the PV arrays.
· Solar DC cables 6mm2 to connect the PVs together and to the inverter directly passing by PV combiner box with all conduits, clamps, trays and cable end terminations which shall be DC plug and socket connectors.
· DC cables must be sized in accordance with the installation requirements applicable on site and must be according to the drawings, specifications and as per the approval.
· Max allowable voltage drops for DC cables between PV Arrays and inverter: 1%
· All works and materials must be according to the drawings, specifications and as per the approval.
· Price includes all works, making good and reinstatement including necessary materials and workmanship to complete the job successfully.
· Min Original PV panels warrantee: 20 years.
· PV must have TUV Rheinland third-party testing and certification ensures that panels comply IEC standards.
PV Characteristics at Standard Test Conditions (STC)
· Standard Test Conditions (STC): irradiance of 1000 W/m2 at spectrum AM 1.5 solar spectrum and temperature 25 ± 2 °C
· Max Power of solar panel (Pmax): at least 650 Watt
· Open Circuit Voltage (Voc): 45 – 50 V
· Short Circuit Current (Isc): 18– 19 A
· Voltage at Max Power (Vmp): 37.5 – 40 V
· Current at Max Power (Imp): <17.5
· Min Module Efficiency not less 20.9 %
· Max system voltage: 1500 V (IEC / UL) or 1000 V (IEC / UL)
· Max series fuse rating: 30A
· Positive power tolerance: 0~+3 to 10%
PV Mechanical Characteristics
· Cell Type: Mono - crystalline
· Frame Material: Anodized aluminum alloy, crossbar enhanced.
· Front cover: not less than 2mm, Anti-Reflection Coating, High Transmission, Low Iron, Tempered Glass.
· Back Glass: not less than 2mm heat strengthened glass.
· Junction Box: IP68, 3 bypass diodes.
· Fire safety Classification: Class C (IEC 61730 or EN 61730)
· IEC classifications: IEC61215/IEC61701/IEC62716/ IEC 60068-2-68
· ISO 9001 quality standards, ISO 14001 environmental standards and ISO 45001 for occupational health & safety.
· Min Static Load Wind pressure capacity: 2400 Pa
Solar Cables
· Color: (Black & Red) or (Blue & Brown)
· Max PV system voltage (DC): 1.6 - 1.8 KV
· Test voltage: 10 KVDC
· Conductor: Electrolytic copper and thin plated
· Insulation: Flame retardant and fire resistant and halogen free
· Sheath: Flame retardant and fire resistant and halogen free
· UV resistant, Acid and base resistant
· Smoke emission: low smoke emission
Earthing for PV Solar System:
· Supply, install, connect and operate complete independent earthing system for PV solar system.
· Earthing system must be separated of the main earthing system to obtain 2-ohm max resistance.
· The item includes (3copper electrodes 15mm2 driven into ground, manholes with cast iron cover (5 Ton) with hinge, earth joints, clamps, ducts, conduits and 50 mm2 flexible earthing copper wires and cables from the PV system components and steel structure to the electrode to complete the system as specifications, drawings and as per the approval.
· For PV solar 10 mm2 flexible earthing copper wires shall be in-between PV panels
· For steel structure 16mm2 flexible earthing copper wires shall be from 3 different points in each string.
PV Modules Subtotal No.1 in EUR |  |  |  |  | 0
2 | PV Combiner Box | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
2.1 | · Supply, install, connect, and operate a PV combiner box for each Inverter, all in accordance with drawings, standards, and the instructions of the supervisor engineer. | Combiner | 10 |  | 0
· Water and dust proof: IP-65
· Material: Aluminum steel case.
· The combiner box shall be installed one for each inverter. There are 4 strings of PV’s connections, each string shall include:
o Double pole DC circuit breaker or Double fuse holder with fuses as required.
o surge arrestor (SPD),
o copper B. Bars, glands, and fixing brackets with rivets.
2.2 | SPD specifications: | No. | 20 |  | 0
· Solar 2P DC SPD Surge protective device, to protect against lighting surge voltages in the solar system.
· Units must be installed in parallel to the DC networks to be protected.
· It shall be installed at the ends of the DC power supply line (solar panel side) and installed inside the control room.
· Equipped with specific thermal disconnectors and related failure indicators.
· Indicator display: (green is OK, red indicates failure)
· Pole: 2P
· Not less than 1000v,40KA
· European type or equivalent.
2.3 | DC Circuit breaker specifications: | No. | 20 |  | 0
· European type or equivalent.
· Pole: 2P
· 800VDC, 25A
PV Combiner Box Subtotal No.2 in EUR |  |  |  |  | 0
3 | Batteries: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
3.1 | · Supply, install, connect, and operate VRLA tubular design deep cycle batteries, European made or equivalent. | KWH | 720 |  | 0
· Valve Regulated Tubular Plate opzv Batteries for Renewable Energy Storage Applications
· Min total demand energy: 144 KWh @ C10, 1.8V per cell for each school
· Battery bank voltage: 48 VDC
· Manufacturing date: less than 6 months upon delivery
· Min Service Life: 10 years
· Internal resistance: 0.1 – 0.15 mΩ
· Case flame retardant & non-hazardous
· Install & connect Battery temp. sensor (BTS)
· Battery must be certified according to IEC standards.
· At least two string batteries style connection.
Battery Specifications:
· Max allowable voltage drop: 1%
· Battery type: Valve Regulated Tubular Plate GEL Batteries for Stand - By Applications, OPZV
· Min Capacity for total batteries bank not less than: 3000 Ah @10hr-rated to 1.80V per cell @ 20 °C for batteries bank as total.
· Max Self-Discharge: 2% per month @ 20°C
· Float charging Voltage (V/Cell): 2.25 VDC / battery Averaged at 20 °C
· Min No. of cycles to reach 60% of Depth of charging: 2500 - 3000 cycle
· Warranty: Two years
· Compliant with IEC 61427 requirements for photovoltaic energy systems
· Tested according to IEC 60896-21 and fully compliant with IEC 60896-22 requirements for valve regulated batteries.
· Full conformity to DIN 40742 specifications for OPzV cells and DIN 40744 for OPzV blocks
· Compliant with the safety requirements of IEC 62485-2 for stationary batteries
· Certified with ISO 9001, ISO 14001, BS OHSAS 18001
· Battery Banks with dividers and all needed accessories to finish the job. The rack must be original and enough to carry all the weight of the required batteries for the system.
· All works and materials must be according to the drawings, specifications and as per the approval.
· The mounting structure of battery banks shall be connected to the earth system with 10mm2 flexible earthing copper wires.
Batteries Subtotal No.3 in EUR |  |  |  |  | 0
4 | Wall Mounted Battery Box: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
4.1 | · Supply, install, connect, and operate battery DC PROTECTION box with all DC circuit breakers required to use as an external DC distributor to protect the battery connections to the inverters. | Battery Box | 5 |  | 0
· The box must be made of galvanized steel 2 mm thick, wall mounting, suitable for connections for three battery inverters
· Waterproof protection with IP65.
· The item includes all necessary and suitable DC cables from the battery bank and to the DC connections box 70 mm2 at least, and from the box to the battery inverters (50mm2 at least) to have a complete operational circuit with all bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations needed to fix it.
· All DC cables must be sized in accordance with the installation requirements applicable on site.
· Max allowable voltage drop: 1%.
· The battery DC protection box shall include at least the following: Galvanized steel panels boards, 2mm with free space up to 50%, 4 LTL fuses disconnectors 630/800 A with 500A Fuses for each, cable glands, Copper Busbars up to 1000 A, and cable end terminations. European type or equivalent.
· Two DC MCB 3X250A/500 VDC/ 50kA, European type or equivalent.
· Warrantee: 5 years
Wall Mounted Battery Box Subtotal No.4 in EUR |  |  |  |  | 0
5 | Inverter – 25KW On Grid | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
5.1 | · Supply, install, connect and operate DC/AC grid-tie 3-phase inverter with data communication unit with Ethernet connection, European type or equivalent. | Inverter | 10 |  | 0
· Indoor and outdoor installations: IP65
· Supply, install and connect monitoring and controlling unit for the solar system to be compatible with the inverters, with all needed accessories, interface modules & data cables and all connections.
· Safety concepts: triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2.
· Inverters shall allow an adjustable power factor Min AC output power with all necessary electrical cables, earthing system, Conduits, trays and all other materials and workmanship needed to connect with the main distribution panel according to the engineer's instruction and approval and have a complete job.
· Min Manufacturer warranty: 5 years
· Max. usable DC power (@ cos ϕ = 1): 25000 W
· Max. generator power: 37500 Wp
· Max. DC voltage: 1000 V
· MPP voltage range / rated input voltage: 430 to 800 V
· Min. input voltage / start input voltage: 150 V /188 V
· Max. input current per MPP tracker / 24 A
· Max. DC short-circuit current per MPP tracker: 37.5 A
· Number of independent MPP trackers / strings per MPP tracker: 3/ 2
· Rated power (at 230 V, 50 Hz): 25000 W
· Max. AC apparent power: 25000 VA
· AC nominal voltage:
· 3 / N / PE; 220 V / 380 V
· 3 / N / PE; 230 V / 400 V
· 3 / N / PE; 240 V / 415 V
· AC voltage range: 176 to 275 V
· Rated power frequency / rated grid voltage 50 Hz / 230 V
· Max. output current / Rated output current: 36.2 A / 36.6 A
· Power factor at rated power / Adjustable displacement power factor: 1 / 0 overexcited to 0 under excited.
· THD: ≤ 3%
· Feed-in phases / connection phases: 3 / 3
· Max. efficiency: not less than 98.2%
The inverter shall include:
· DC-side disconnection device
· Ground fault monitoring / grid monitoring
· DC reverse polarity protection / AC short-circuit current capability.
· All-pole sensitive residual - current monitoring unit
· Protection class: IEC 62109-1
· overvoltage category (according to IEC 62109-1): I / AC: III; DC: II
· Degree of protection (as per IEC 60529): IP65
· Climatic category (according to IEC 60721-3-4): 4K4H
· Supply, install, connect and operate one PV combiner box for both Inverters, Water and dust proof: IP-65, Material: Aluminum steel case, one DC MCB2x25A for each string s of PV’s including copper B. Bars, glands, and all other needed to make job ready .
Inverter – 25KW On Grid Subtotal No.5 in EUR |  |  |  |  | 0
6 | 15 KVA Battery Inverter: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
6.1 | · Supply, install, connect and operate Battery Inverter compatible with on grid inverters with all necessary interface modules and connections for masters & slaves, electrical cables, materials and data communication unit, router with Ethernet connection, connectable in parallel and modularly extendable. | Inverter | 15 |  | 0
· Battery Inverter must include AC and DC coupling, High efficiency, intelligent battery management for Max battery life, charge level calculation, extreme overload capability, and battery temperature sensing and battery current measurements.
· Price includes supply, install and connect Remote Control Units for the installed battery inverters and On-site Monitoring and control to Monitor and control. Locally, and also remotely with all data & communication cables and connection needed to complete the job.
· AC electrical cables to connect battery inverters with main distribution panel (AC Out).
· Works include all conduits, clamps, trays, B. Bars and cable terminations end and workmanship needed to have a complete job.
· The price shall include supply, install and connect Color Control GX and other GX devices For Monitoring and control Locally and also remotely, VE. Bus to USB interface, VE. Bus to NMEA 2000 interface, VE. Bus Smart Dongle, and Smart Battery Monitor.
· Max allowable voltage drops for DC cables between battery inverter and batteries: 1%
· Min Manufacturer warranty: 5 years
General Specifications:
· Battery Inverter shall include Power Control / Power Assist
· Battery Inverter shall include Integrated Transfer switch.
· Input voltage range: 187 - 265 VAC
· Input frequency: 45 – 65 Hz
· Power factor: 1
· Operating temp.: -40 to +65˚C
· Max Humidity (non-condensing): 95%
· Max feed through current: 2x100 A
· Auxiliary output Switches off when no external AC source available: 50 A
· Programmable relay that can be set for general alarm.
· DC under voltage or genset start/stop function.
· AC rating: 230 V / 4 A
· DC rating: 4 A up to 35 VDC, 1 A up to 60 VDC
· VE. Bus communication port: For parallel and three phase operation, remote monitoring, and system integration
· Have Remote on-off
· Input voltage range (VDC): 9.5 – 17V, 19 – 33V, 38 – 66V
· Output voltage: 230 VAC ± 2%
· Output frequency: 50 Hz ± 0.1%
· Cont. output power at 25°C (VA) at non-linear load, crest factor: 15000 VA
· Cont. output power at 25°C: 12000W
· Cont. output power at 40°C: 10000W
· Cont. output power at 65°C: 7000W
· Peak power: 25000W
· Max efficiency: 96%
· Zero load power: 110W
· Zero load power in AES mode: 75W
· Zero load power in Search mode: 20W
Charger Specifications:
· Charge voltage 'absorption' (VDC): 57.6
· Charge voltage 'float' (V DC): 55.2
· Storage mode (VDC): 52.8
· Charge current house battery at 25˚C ambient: 200A
· Have Battery temperature sensor.
Other specifications:
· Protection category: IP 21
· Safety standard: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1
· Emission, Immunity EN 55014 standards: EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, EN-IEC 61000-3-3, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3.
15 KVA Battery Inverter Subtotal No.6 in EUR |  |  |  |  | 0
7 | AC panel: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
7.1 | · Supply, install, test, and commission AC protected loads panel with all required AC bus bars AC cables, conduits, cable trays, protections including MCCB, MCB, RCD, SPD, and all other material needed to have a complete job ready for protected load powering according to the engineer’s instructions and approval drawings. | Lump Sum | 5 |  | 0
· The loads panel shall have 30% extra space for future extension, the panel made of galvanized steel sheet and frame 2mm thick, painted with anti-static primer paint and 2 coats of final polyester paint with two doors.
· The panel shall be factory assembled c/w pvc coated Cu bus bars of adequate sizes and all other accessories and civil works that may needed to complete the job and hand over in operable conditions trenches, power and control wires, terminals bus bars neutral bus bar, earthing bus bar ducts, supports, labels and numbers and all necessary accessories to complete the work. According to Standards, drawings, specifications and supervisor engineer instructions.
· The panel including but not limited the following:
o Molded Case Circuit Breaker MCCB 4X63A/NZMB-63A (no.3)
o One Phase Sequence
o One Over Voltage, Under Voltage, OF and UF protections.
o 4 unit Signal indication lamps RST (Two sets) with resistance 220V, with LTL fuses (3*32/6A) for IN and Out.
o 3-phase digital KWH meter (two sets), with all CT's and any other material needed to have a complete job. The KWh meter has monitoring LCD with all needed data & interface cables to connect with the Monitoring System.
o Two copper Busbars for IN and OUT (250A rated)
o AC earthing system. - XLPE/PVC/Cu 5x10 mm2 and 5x16mm2 cable for inverters IN and OUT.
o AC surge arrestor 40KA, 4P.
o Miniature Circuit Breaker MCB 3X10A Isc=10kA (two No’s) for Ac out from battery inverter.
o Miniature Circuit Breaker MCB 2X63A Isc=10kA (3 No’s) for Ac in from battery inverter.
o Miniature Circuit Breaker MCB 2X50A Isc=10kA (3 No’s) for Ac in from battery inverter.
o Miniature Circuit Breaker MCB 4X40A Isc=10kA (two No’s) for Ac out from inverter.
o Digital multimeter (2 set) with accessories.
o Contactor for load shedding 3*63A.
o Residual current circuit breaker RCD 4X40/0.03A (two set) for Ac out from inverter.
· The cable size as drawing in SLD and According to Standards, specifications and supervisor engineer instructions.
· The items in general shall also include conduits, connection boxes, controls, wires, connectors, clamps, bolts, and connecting the cables to switchboards and main Solar MDB are included in the unit price.
· Supply & Install Manual Transfer Switch (MTS) 100 A- 400V complete and approved equivalent with all needed fittings and accessories to get job ready according to specifications and supervisor engineer instructions.
· The contractor shall submit shop drawing for AC panel with dimensions.
· Price includes all necessary civil works, cables connection between panels, ducts, and all needed accessories to operate and finish the job.
· The existing electrical boards must be rearranged as per instructions and the contractor must take into consideration the Loads' cables.
AC panel Subtotal No.7 in EUR |  |  |  |  | 0
8 | CABLES AND CODUITES | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
8.1 | · Supply, laying and termination of XLPE Cu cable5x16 mm2 with all needed accessories to fixing and operate | L.M. | 500 |  | 0
8.2 | · Ditto, but XLPE Cu Cable 5x10mm2. | L.M. | 1000 |  | 0
8.3 | · Ditto, but Fileable Cable 3x10 mm2, for SDB in Batteries Room. | L.M. | 150 |  | 0
8.4 | · Supply, lay the underground piping 2x6" include the excavation in all soil type to the level varies between 0.8 to 1.0 meters below the finish ground level, the pipes shall be for the electric power AC cables made of UPVC (SN8) c/w sleeves, elbows of different angles, etc. 10cm od clean sand to be under and above the pipes in the excavated trench and the pipes will also be protected with concrete tiles of thickness not less that 5cm, install warning tape of approved materials with text in both Arabic and English warning of electric cables below at 40cm from ground, backfilling to restore the soil to its natural case. the price includes reinstatement of existing interlock or tiles. | L.M. | 250 |  | 0
8.5 | · Supply, install (20cmx8cm), 1.5mm thickness hot dip galvanized steel perforated cable trays with cover, bends, T derivation, reducers and fixing accessories The tray will be installed from Combiner boxes and PV inverters and for AC cables on rooftop/walls. (Type is OBO or equivalent) | L.M. | 500 |  | 0
CABLES AND CODUITES Subtotal No. 8 in EUR |  |  |  |  | 0
9 | Smart AC Air Condition: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
9.1 | · Supply, install, test and commission 4 unit air conditioning Inverter type Split Unit work as alternate operation, composed of indoor and outdoor units. filled with environment friendly refrigerant such as (R410, R407c,..) and COP not less than 3.5,Condensing unit shall be complete with Inverter compressor/s & air cooled condenser with fan, Well supported on hot galvanized steel base on the roof, indoor unit with plasma filter as indicated on drawings to be tights installed completed with all necessary supports, hangers, drain pipes from indoor unit to the nearest floor drain, ( PVC Ø 1"), cupper pipes , sleeves, thermostat , Remote control. | Set | 5 |  | 0
· The price including Isolation Switch, separate control system, Plastic panel 24C.B Capacity, thermostat digital type, timers, contactors and all required electrical power and control cables from SDB to the unit according to drawings and engineers approval.
· Capacity: 18000 BTU/HR for each condition
· Filled with environment friendly refrigerant such as (R410, R407c,..)
· Min COP: 3.8
· The condensing unit shall be complete with Inverter compressor/s & air-cooled condenser with fan.
· Installed completed with all necessary supports, hangers, drainpipes from indoor unit to the nearest floor drain, cupper pipes, sleeves, thermostat, Remote control and including Isolation Switch and all required electrical power cables from SDB to the units.
· The installation shall include the following:
o 4 contactor 3x20A
o 4 MCB 2x20A
o 2 timers 24H
o 2RCD 2x40A
o Suitable size of AC protected loads panel.
o Loads panel shall have 30% extra space for future extension, the panel made of galvanized steel sheet and frame 2mm thick, painted with anti-static primer paint and 2 coats of final polyester paint.
· To ensure that the air conditions operate alternately for 12 hours for each group air condition as in SLD, including all required AC bus bars AC cables, conduits, cable trays, protections including MCCB, MCB, RCD, contactor, timers , wires and all other material needed to have a complete job ready according to the engineer’s instructions and approval drawings.
Smart AC Air Condition Subtotal No. 9 in EUR |  |  |  |  | 0
10 | PV Mounting Structure | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
10.1 | · Material: Hot dip galvanized steel structure sized to the dimensions of the selected PV modules and PV numbers using recommended profiles shapes 4cm*8cm*2.7mm, 4cm*4cm*2.7mm, 6cm*6cm*2.7mm. | LS | 5 |  | 0
· Final dimensions of the attached structure are subject to change upon delivery of the PV panels.
· Vertical supports, screws, and 4-5 mm min thick steel plates for each leg or concrete bases as per the attached drawings.
· The mounting structure of PV’s shall be connected with the PV’s earthing system.
· All nuts & bolts shall be made of galvanized or stainless steel.
· The legs of the mounting structure shall be surrounded with concrete base B250, 30cmX30cmX30cm.
· The structure shall be designed to resist wind speed more than 150 km/h allowing easy replacement of any module in line with site requirements.
· Modules alignment shall be 30º - 32° tilt angle to provide the maximum annual energy output.
· The structure shall absorb and transfer the mechanical loads to the ground properly.
Mounting Structure painting:
· The surface shall be dry and clean before painting.
· All painting works shall provide the required coverage.
· Supply and paint one prime coat and let dry; in addition to minimum two extra coats using paints specialized made for galvanized surfaces according to supervisor instructions and MOHE requirements.
· The price shall include all other material needed to have a complete job ready according to the engineer’s instruction, approval, and drawings.
PV Mounting Structure Subtotal No. 10 in EUR |  |  |  |  | 0
11 | MISCELLANEOUS ELECTRICAL WORKS | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
11.1 | Supply, install, connect, and test AC LED tube lamp T8, 120 cm, 18W, 6500k, Cap-Base G13,160-240 Volt, not less than 15000H lifetime, with 0.95 PF at least, Efficacy more than 100 Lm/W. The price includes dismantling the existing fluorescent lamps, ballasts, condensers and rewiring to be compatible with instant Start and allows fixture to maintain original compliance. All works and materials shall be according to standards and specifications and the approval of the supervisor engineer. All the dismantled fluorescent lamps, starter, chock coil shall be handed over to the MoE. Type PHILIPS or equivalent). | No. | 1200 |  | 0
11.2 | Supply, install, connect, and test AC LED Lamp 15W for existing Globe lighting. The price includes dismantling the existing old lamps. All works and materials shall be according to standards and specifications and the approval of the supervisor engineer. All the dismantle old lamps shall be handed over to the MoE. Type PHILIPS or equivalent. | No. | 240 |  | 0
11.3 | Supply and install Manual (CO2 Gas) wall mounted Fire extinguisher (6kg) with all accessories, fittings and all required works to complete the job. | Unit | 4 |  | 0
11.4 | Ditto but for Manual (Dry Powder) Fire extinguisher (6kg). | Unit | 4 |  | 0
11.5 | Supply and install Automatic (Halotron Agent) hanged Fire extinguisher (6kg) with thermal hose to every component in the panel. The item includes all accessories, fittings, and all required works to complete the job. | Unit | 8 |  | 0
11.6 | Supply Clamp Meter 1000 V and 1000 A in both ac and dc modes. Additionally flexible current probe expanding. | No | 2 |  | 0
Measurement capability
· 1000 Aa can current measurement with fixed jaw
· 2500 Aac current measurement with flexible current probe
· 1000Vac and dc voltage measurement
· Frequency measurement to 500Hz
· 60kΩ resistance measurement with continuity detection
· 500mVdc measurement range to interface with other accessories
· 1000μF capacitance measurement
11.7 | Cordless screwdriver with two original batteries and charger. | No | 2 |  | 0
MISCELLANEOUS ELECTRICAL WORKS Subtotal No. 11 in EUR |  |  |  |  | 0
Grand Total for Lot 1 in EUR |  |  |  |  | 0

## LOT 2 - BOQ
PUBLIC PROCUREMENT CONTRACT FOR SUPPLY AND INSTALLATION OF ROOF-TOP SOLAR PHOTOVOLTAIC SYSTEMS ON SCHOOLS IN GAZA STRIP
TENDER NO. PZA1203211-10026
ANNEX 1 – BILL OF QUANTITIES
LOT 2 - FIVE SCHOOLS WITH 39 KW PV MODULES
ABU ZAR EL GEFARI SCHOOL, KHALIL ELNOBANI HIGH SCHOOL, MOHAMMED EL NAGAR HIGH SCHOOL, EL MOTANABI HIGH SCHOOL, OM EL FAHEM HIGH SCHOOL
1 | PV Modules: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
1.1 | Supply, install, connect, and operate BIFACIAL MONO PV Solar Modules (Min total arrays capacity not less 39KWp for each school). The item includes the supply, installation, and connection of the following: | KWp | 195 |  | 0
· PVC ducts with clamps, accessories, supports & labels suitable to be installed under the PV arrays.
· Solar DC cables 6mm2 to connect the PVs together and to the inverter directly passing by PV combiner box with all conduits, clamps, trays and cable end terminations which shall be DC plug and socket connectors.
· DC cables must be sized in accordance with the installation requirements applicable on site and must be according to the drawings, specifications and as per the approval.
· Max allowable voltage drops for DC cables between PV Arrays and inverter: 1%
· All works and materials must be according to the drawings, specifications and as per the approval.
· Price includes all works, making good and reinstatement including necessary materials and workmanship to complete the job successfully.
· Min Original PV panels warrantee: 20 years.
· PV must have TUV Rheinland third-party testing and certification ensures that panels comply IEC standards.
PV Characteristics at Standard Test Conditions (STC)
· Standard Test Conditions (STC): irradiance of 1000 W/m2 at spectrum AM 1.5 solar spectrum and temperature 25 ± 2 °C
· Max Power of solar panel (Pmax): at least 650 Watt
· Open Circuit Voltage (Voc): 45 – 50 V
· Short Circuit Current (Isc): 18– 19 A
· Voltage at Max Power (Vmp): 37.5 – 40 V
· Current at Max Power (Imp): <17.5
· Min Module Efficiency not less 20.9 %
· Max system voltage: 1500 V (IEC / UL) or 1000 V (IEC / UL)
· Max series fuse rating: 30A
· Positive power tolerance: 0~+3 to 10%
PV Mechanical Characteristics
· Cell Type: Mono - crystalline
· Frame Material: Anodized aluminum alloy, crossbar enhanced.
· Front cover: not less than 2mm, Anti-Reflection Coating, High Transmission, Low Iron, Tempered Glass.
· Back Glass: not less than 2mm heat strengthened glass.
· Junction Box: IP68, 3 bypass diodes.
· Fire safety Classification: Class C (IEC 61730 or EN 61730)
· IEC classifications: IEC61215/IEC61701/IEC62716/ IEC 60068-2-68
· ISO 9001 quality standards, ISO 14001 environmental standards and ISO 45001 for occupational health & safety.
· Min Static Load Wind pressure capacity: 2400 Pa
Solar Cables
· Color: (Black & Red) or (Blue & Brown)
· Max PV system voltage (DC): 1.6 - 1.8 KV
· Test voltage: 10 KVDC
· Conductor: Electrolytic copper and thin plated
· Insulation: Flame retardant and fire resistant and halogen free
· Sheath: Flame retardant and fire resistant and halogen free
· UV resistant, Acid and base resistant
· Smoke emission: low smoke emission
Earthing for PV Solar System:
· Supply, install, connect and operate complete independent earthing system for PV solar system.
· Earthing system must be separated of the main earthing system to obtain 2-ohm max resistance.
· The item includes (3copper electrodes 15mm2 driven into ground, manholes with cast iron cover (5 Ton) with hinge, earth joints, clamps, ducts, conduits and 50 mm2 flexible earthing copper wires and cables from the PV system components and steel structure to the electrode to complete the system as specifications, drawings and as per the approval.
· For PV solar 10 mm2 flexible earthing copper wires shall be in-between PV panels
· For steel structure 16mm2 flexible earthing copper wires shall be from 3 different points in each string.
PV Modules Subtotal No.1 in EUR |  |  |  |  | 0
2 | PV Combiner Box | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
2.1 | · Supply, install, connect, and operate a PV combiner box for each Inverter, all in accordance with drawings, standards, and the instructions of the supervisor engineer. | Combiner | 10 |  | 0
· Water and dust proof: IP-65
· Material: Aluminum steel case.
· The combiner box shall be installed one for each inverter. There are 4 strings of PV’s connections, each string shall include:
o Double pole DC circuit breaker or Double fuse holder with fuses as required.
o surge arrestor (SPD),
o copper B. Bars, glands, and fixing brackets with rivets.
2.2 | SPD specifications: | No. | 20 |  | 0
· Solar 2P DC SPD Surge protective device, to protect against lighting surge voltages in the solar system.
· Units must be installed in parallel to the DC networks to be protected.
· It shall be installed at the ends of the DC power supply line (solar panel side) and installed inside the control room.
· Equipped with specific thermal disconnectors and related failure indicators.
· Indicator display: (green is OK, red indicates failure)
· Pole: 2P
· Not less than 1000v,40KA
· European type or equivalent.
2.3 | DC Circuit breaker specifications: | No. | 20 |  | 0
· European type or equivalent.
· Pole: 2P
· 800VDC, 25A
PV Combiner Box Subtotal No.2 in EUR |  |  |  |  | 0
3 | Batteries: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
3.1 | · Supply, install, connect, and operate VRLA tubular design deep cycle batteries, European made or equivalent. | KWH | 528 |  | 0
· Valve Regulated Tubular Plate opzv Batteries for Renewable Energy Storage Applications
· Min total demand energy: 105.6 KWh @ C10, 1.8V per cell for each school
· Battery bank voltage: 48 VDC
· Manufacturing date: less than 6 months upon delivery
· Min Service Life: 10 years
· Internal resistance: 0.1 – 0.15 mΩ
· Case flame retardant & non-hazardous
· Install & connect Battery temp. sensor (BTS)
· Battery must be certified according to IEC standards.
· At least two string batteries style connection.
Battery Specifications:
· Max allowable voltage drop: 1%
· Battery type: Valve Regulated Tubular Plate GEL Batteries for Stand - By Applications, OPZV
· Min Capacity for total batteries bank not less than: 2200 Ah @10hr-rated to 1.80V per cell @ 20 °C for batteries bank as total.
· Max Self-Discharge: 2% per month @ 20°C
· Float charging Voltage (V/Cell): 2.25 VDC / battery Averaged at 20 °C
· Min No. of cycles to reach 60% of Depth of charging: 2500 - 3000 cycle
· Warranty: Two years
· Compliant with IEC 61427 requirements for photovoltaic energy systems
· Tested according to IEC 60896-21 and fully compliant with IEC 60896-22 requirements for valve regulated batteries.
· Full conformity to DIN 40742 specifications for OPzV cells and DIN 40744 for OPzV blocks
· Compliant with the safety requirements of IEC 62485-2 for stationary batteries
· Certified with ISO 9001, ISO 14001, BS OHSAS 18001
· Battery Banks with dividers and all needed accessories to finish the job. The rack must be original and enough to carry all the weight of the required batteries for the system.
· All works and materials must be according to the drawings, specifications and as per the approval.
· The mounting structure of battery banks shall be connected to the earth system with 10mm2 flexible earthing copper wires.
Batteries Subtotal No.3 in EUR |  |  |  |  | 0
4 | Wall Mounted Battery Box: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
4.1 | · Supply, install, connect, and operate battery DC PROTECTION box with all DC circuit breakers required to use as an external DC distributor to protect the battery connections to the inverters. | Battery Box | 5 |  | 0
· The box must be made of galvanized steel 2 mm thick, wall mounting, suitable for connections for three battery inverters
· Waterproof protection with IP65.
· The item includes all necessary and suitable DC cables from the battery bank and to the DC connections box 70 mm2 at least, and from the box to the battery inverters (50mm2 at least) to have a complete operational circuit with all bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations needed to fix it.
· All DC cables must be sized in accordance with the installation requirements applicable on site.
· Max allowable voltage drop: 1%.
· The battery DC protection box shall include at least the following: Galvanized steel panels boards, 2mm with free space up to 50%, 4 LTL fuses disconnectors 630/800 A with 500A Fuses for each, cable glands, Copper Busbars up to 1000 A, and cable end terminations. European type or equivalent.
· Two DC MCB 3X200A/500 VDC/ 50kA, European type or equivalent.
· Warrantee: 5 years
Wall Mounted Battery Box Subtotal No.4 in EUR |  |  |  |  | 0
5 | Inverter – 20KW On Grid | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
5.1 | · Supply, install, connect and operate DC/AC grid-tie 3-phase inverter with data communication unit with Ethernet connection, European type or equivalent. | Inverter | 10 |  | 0
· Indoor and outdoor installations: IP65
· Supply, install and connect monitoring and controlling unit for the solar system to be compatible with the inverters, with all needed accessories, interface modules & data cables and all connections.
· Safety concepts: triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2.
· Inverters shall allow an adjustable power factor Min AC output power with all necessary electrical cables, earthing system, Conduits, trays and all other materials and workmanship needed to connect with the main distribution panel according to the engineer's instruction and approval and have a complete job.
· Min Manufacturer warranty: 5 years
· Max. usable DC power (@ cos ϕ = 1): 20000 W
· Max. generator power: 30000 Wp
· Max. DC voltage: 1000 V
· MPP voltage range / rated input voltage: 345 to 800 V
· Min. input voltage / start input voltage: 150 V /188 V
· Max. input current per MPP tracker / 24 A
· Max. DC short-circuit current per MPP tracker: 37.5 A
· Number of independent MPP trackers / strings per MPP tracker: 3/ 2
· Rated power (at 230 V, 50 Hz): 20000 W
· Max. AC apparent power: 20000 VA
· AC nominal voltage:
· 3 / N / PE; 220 V / 380 V
· 3 / N / PE; 230 V / 400 V
· 3 / N / PE; 240 V / 415 V
· AC voltage range: 176 to 275 V
· Rated power frequency / rated grid voltage 50 Hz / 230 V
· Max. output current / Rated output current: 29 A / 36.6 A
· Power factor at rated power / Adjustable displacement power factor: 1 / 0 overexcited to 0 under excited.
· THD: ≤ 3%
· Feed-in phases / connection phases: 3 / 3
· Max. efficiency: not less than 98.2%
The inverter shall include:
· DC-side disconnection device
· Ground fault monitoring / grid monitoring
· DC reverse polarity protection / AC short-circuit current capability.
· All-pole sensitive residual - current monitoring unit
· Protection class: IEC 62109-1
· overvoltage category (according to IEC 62109-1): I / AC: III; DC: II
· Degree of protection (as per IEC 60529): IP65
· Climatic category (according to IEC 60721-3-4): 4K4H
· Supply, install, connect and operate one PV combiner box for both Inverters, Water and dust proof: IP-65, Material: Aluminum steel case, one DC MCB2x25A for each string s of PV’s including copper B. Bars, glands, and all other needed to make job ready .
Inverter – 20KW On Grid Subtotal No.5 in EUR |  |  |  |  | 0
6 | 15 KVA Battery Inverter: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
6.1 | · Supply, install, connect and operate Battery Inverter compatible with on grid inverters with all necessary interface modules and connections for masters & slaves, electrical cables, materials and data communication unit, router with Ethernet connection, connectable in parallel and modularly extendable. | Inverter | 15 |  | 0
· Battery Inverter must include AC and DC coupling, High efficiency, intelligent battery management for Max battery life, charge level calculation, extreme overload capability, and battery temperature sensing and battery current measurements.
· Price includes supply, install and connect Remote Control Units for the installed battery inverters and On-site Monitoring and control to Monitor and control. Locally, and also remotely with all data & communication cables and connection needed to complete the job.
· AC electrical cables to connect battery inverters with main distribution panel (AC Out).
· Works include all conduits, clamps, trays, B. Bars and cable terminations end and workmanship needed to have a complete job.
· The price shall include supply, install and connect Color Control GX and other GX devices For Monitoring and control Locally and also remotely, VE. Bus to USB interface, VE. Bus to NMEA 2000 interface, VE. Bus Smart Dongle, and Smart Battery Monitor.
· Max allowable voltage drops for DC cables between battery inverter and batteries: 1%
· Min Manufacturer warranty: 5 years
General Specifications:
· Battery Inverter shall include Power Control / Power Assist
· Battery Inverter shall include Integrated Transfer switch.
· Input voltage range: 187 - 265 VAC
· Input frequency: 45 – 65 Hz
· Power factor: 1
· Operating temp.: -40 to +65˚C
· Max Humidity (non-condensing): 95%
· Max feed through current: 2x100 A
· Auxiliary output Switches off when no external AC source available: 50 A
· Programmable relay that can be set for general alarm.
· DC under voltage or genset start/stop function.
· AC rating: 230 V / 4 A
· DC rating: 4 A up to 35 VDC, 1 A up to 60 VDC
· VE. Bus communication port: For parallel and three phase operation, remote monitoring, and system integration
· Have Remote on-off
· Input voltage range (VDC): 9.5 – 17V, 19 – 33V, 38 – 66V
· Output voltage: 230 VAC ± 2%
· Output frequency: 50 Hz ± 0.1%
· Cont. output power at 25°C (VA) at non-linear load, crest factor: 15000 VA
· Cont. output power at 25°C: 12000W
· Cont. output power at 40°C: 10000W
· Cont. output power at 65°C: 7000W
· Peak power: 25000W
· Max efficiency: 96%
· Zero load power: 110W
· Zero load power in AES mode: 75W
· Zero load power in Search mode: 20W
Charger Specifications:
· Charge voltage 'absorption' (VDC): 57.6
· Charge voltage 'float' (V DC): 55.2
· Storage mode (VDC): 52.8
· Charge current house battery at 25˚C ambient: 200A
· Have Battery temperature sensor.
Other specifications:
· Protection category: IP 21
· Safety standard: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1
· Emission, Immunity EN 55014 standards: EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, EN-IEC 61000-3-3, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3.
15 KVA Battery Inverter Subtotal No.6 in EUR |  |  |  |  | 0
7 | AC panel: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
7.1 | · Supply, install, test, and commission AC protected loads panel with all required AC bus bars AC cables, conduits, cable trays, protections including MCCB, MCB, RCD, SPD, and all other material needed to have a complete job ready for protected load powering according to the engineer’s instructions and approval drawings. | Lump Sum | 5 |  | 0
· The loads panel shall have 30% extra space for future extension, the panel made of galvanized steel sheet and frame 2mm thick, painted with anti-static primer paint and 2 coats of final polyester paint with two doors.
· The panel shall be factory assembled c/w pvc coated Cu bus bars of adequate sizes and all other accessories and civil works that may needed to complete the job and hand over in operable conditions trenches, power and control wires, terminals bus bars neutral bus bar, earthing bus bar ducts, supports, labels and numbers and all necessary accessories to complete the work. According to Standards, drawings, specifications and supervisor engineer instructions.
· The panel including but not limited the following:
o Molded Case Circuit Breaker MCCB 4X63A/NZMB-63A (no.3)
o One Phase Sequence
o One Over Voltage, Under Voltage, OF and UF protections.
o 4 unit Signal indication lamps RST (Two sets) with resistance 220V, with LTL fuses (3*32/6A) for IN and Out.
o 3-phase digital KWH meter (two sets), with all CT's and any other material needed to have a complete job. The KWh meter has monitoring LCD with all needed data & interface cables to connect with the Monitoring System.
o Two copper Busbars for IN and OUT (250A rated)
o AC earthing system. - XLPE/PVC/Cu 5x10 mm2 and 5x16mm2 cable for inverters IN and OUT.
o AC surge arrestor 40KA, 4P.
o Miniature Circuit Breaker MCB 3X10A Isc=10kA (two No’s) for Ac out from battery inverter.
o Miniature Circuit Breaker MCB 2X50A Isc=10kA (3 No’s) for Ac in from battery inverter.
o Miniature Circuit Breaker MCB 2X40A Isc=10kA (3 No’s) for Ac out from inverter.
o Miniature Circuit Breaker MCB 4X32A Isc=10kA (two No’s) for Ac out from inverter.
o Digital multimeter (2 set) with accessories.
o Contactor for load shedding 3*50A.
o Residual current circuit breaker RCD 4X40/0.03A (two set) for Ac out from inverter.
· The cable size as drawing in SLD and According to Standards, specifications and supervisor engineer instructions.
· The items in general shall also include conduits, connection boxes, controls, wires, connectors, clamps, bolts, and connecting the cables to switchboards and main Solar MDB are included in the unit price.
· Supply & Install Manual Transfer Switch (MTS) 63 A- 400V complete and approved equivalent with all needed fittings and accessories to get job ready according to specifications and supervisor engineer instructions.
· The contractor shall submit shop drawing for AC panel with dimensions.
· Price includes all necessary civil works, cables connection between panels, ducts, and all needed accessories to operate and finish the job.
· The existing electrical boards must be rearranged as per instructions and the contractor must take into consideration the Loads' cables.
AC panel Subtotal No.7 in EUR |  |  |  |  | 0
8 | CABLES AND CODUITES | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
8.1 | · Supply, laying and termination of XLPE Cu cable5x16 mm2 with all needed accessories to fixing and operate | L.M. | 500 |  | 0
8.2 | · Ditto, but XLPE Cu Cable 5x10mm2. | L.M. | 1000 |  | 0
8.3 | · Ditto, but Fileable Cable 3x10 mm2, for SDB in Batteries Room. | L.M. | 150 |  | 0
8.4 | · Supply, lay the underground piping 2x6" include the excavation in all soil type to the level varies between 0.8 to 1.0 meters below the finish ground level, the pipes shall be for the electric power AC cables made of UPVC (SN8) c/w sleeves, elbows of different angles, etc. 10cm od clean sand to be under and above the pipes in the excavated trench and the pipes will also be protected with concrete tiles of thickness not less that 5cm, install warning tape of approved materials with text in both Arabic and English warning of electric cables below at 40cm from ground, backfilling to restore the soil to its natural case. the price includes reinstatement of existing interlock or tiles. | L.M. | 250 |  | 0
8.5 | · Supply, install (20cmx8cm), 1.5mm thickness hot dip galvanized steel perforated cable trays with cover, bends, T derivation, reducers and fixing accessories The tray will be installed from Combiner boxes and PV inverters and for AC cables on rooftop/walls. (Type is OBO or equivalent) | L.M. | 500 |  | 0
CABLES AND CODUITES Subtotal No. 8 in EUR |  |  |  |  | 0
9 | Smart AC Air Condition: | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
9.1 | · Supply, install, test and commission 4 unit air conditioning Inverter type Split Unit work as alternate operation, composed of indoor and outdoor units. filled with environment friendly refrigerant such as (R410, R407c,..) and COP not less than 3.5,Condensing unit shall be complete with Inverter compressor/s & air cooled condenser with fan, Well supported on hot galvanized steel base on the roof, indoor unit with plasma filter as indicated on drawings to be tights installed completed with all necessary supports, hangers, drain pipes from indoor unit to the nearest floor drain, ( PVC Ø 1"), cupper pipes , sleeves, thermostat , Remote control. | Set | 5 |  | 0
· The price including Isolation Switch, separate control system, Plastic panel 24C.B Capacity, thermostat digital type, timers, contactors and all required electrical power and control cables from SDB to the unit according to drawings and engineers approval.
· Capacity: 18000 BTU/HR for each condition
· Filled with environment friendly refrigerant such as (R410, R407c,..)
· Min COP: 3.8
· The condensing unit shall be complete with Inverter compressor/s & air-cooled condenser with fan.
· Installed completed with all necessary supports, hangers, drainpipes from indoor unit to the nearest floor drain, cupper pipes, sleeves, thermostat, Remote control and including Isolation Switch and all required electrical power cables from SDB to the units.
· The installation shall include the following:
o 4 contactor 3x20A
o 4 MCB 2x20A
o 2 timers 24H
o 2RCD 2x40A
o Suitable size of AC protected loads panel.
o Loads panel shall have 30% extra space for future extension, the panel made of galvanized steel sheet and frame 2mm thick, painted with anti-static primer paint and 2 coats of final polyester paint.
· To ensure that the air conditions operate alternately for 12 hours for each group air condition as in SLD, including all required AC bus bars AC cables, conduits, cable trays, protections including MCCB, MCB, RCD, contactor, timers , wires and all other material needed to have a complete job ready according to the engineer’s instructions and approval drawings.
Smart AC Air Condition Subtotal No. 9 in EUR |  |  |  |  | 0
10 | PV Mounting Structure | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
10.1 | · Material: Hot dip galvanized steel structure sized to the dimensions of the selected PV modules and PV numbers using recommended profiles shapes 4cm*8cm*2.7mm, 4cm*4cm*2.7mm, 6cm*6cm*2.7mm. | LS | 5 |  | 0
· Final dimensions of the attached structure are subject to change upon delivery of the PV panels.
· Vertical supports, screws, and 4-5 mm min thick steel plates for each leg or concrete bases as per the attached drawings.
· The mounting structure of PV’s shall be connected with the PV’s earthing system.
· All nuts & bolts shall be made of galvanized or stainless steel.
· The legs of the mounting structure shall be surrounded with concrete base B250, 30cmX30cmX30cm.
· The structure shall be designed to resist wind speed more than 150 km/h allowing easy replacement of any module in line with site requirements.
· Modules alignment shall be 30º - 32° tilt angle to provide the maximum annual energy output.
· The structure shall absorb and transfer the mechanical loads to the ground properly.
Mounting Structure painting:
· The surface shall be dry and clean before painting.
· All painting works shall provide the required coverage.
· Supply and paint one prime coat and let dry; in addition to minimum two extra coats using paints specialized made for galvanized surfaces according to supervisor instructions and MOHE requirements.
· The price shall include all other material needed to have a complete job ready according to the engineer’s instruction, approval, and drawings.
PV Mounting Structure Subtotal No. 10 in EUR |  |  |  |  | 0
11 | MISCELLANEOUS ELECTRICAL WORKS | Unit | Qty. | Unit Price (EUR) | Total Price (EUR)
11.1 | Supply, install, connect, and test AC LED tube lamp T8, 120 cm, 18W, 6500k, Cap-Base G13,160-240 Volt, not less than 15000H lifetime, with 0.95 PF at least, Efficacy more than 100 Lm/W. The price includes dismantling the existing fluorescent lamps, ballasts, condensers and rewiring to be compatible with instant Start and allows fixture to maintain original compliance. All works and materials shall be according to standards and specifications and the approval of the supervisor engineer. All the dismantled fluorescent lamps, starter, chock coil shall be handed over to the MoE. Type PHILIPS or equivalent). | No. | 1200 |  | 0
11.2 | Supply, install, connect, and test AC LED Lamp 15W for existing Globe lighting. The price includes dismantling the existing old lamps. All works and materials shall be according to standards and specifications and the approval of the supervisor engineer. All the dismantle old lamps shall be handed over to the MoE. Type PHILIPS or equivalent. | No. | 240 |  | 0
11.3 | Supply and install Manual (CO2 Gas) wall mounted Fire extinguisher (6kg) with all accessories, fittings and all required works to complete the job. | Unit | 4 |  | 0
11.4 | Ditto but for Manual (Dry Powder) Fire extinguisher (6kg). | Unit | 4 |  | 0
11.5 | Supply and install Automatic (Halotron Agent) hanged Fire extinguisher (6kg) with thermal hose to every component in the panel. The item includes all accessories, fittings, and all required works to complete the job. | Unit | 8 |  | 0
11.6 | Supply Clamp Meter 1000 V and 1000 A in both ac and dc modes. Additionally flexible current probe expanding. | No | 2 |  | 0
Measurement capability
· 1000 Aa can current measurement with fixed jaw
· 2500 Aac current measurement with flexible current probe
· 1000Vac and dc voltage measurement
· Frequency measurement to 500Hz
· 60kΩ resistance measurement with continuity detection
· 500mVdc measurement range to interface with other accessories
· 1000μF capacitance measurement
11.7 | Cordless screwdriver with two original batteries and charger. | No | 2 |  | 0
MISCELLANEOUS ELECTRICAL WORKS Subtotal No. 11 in EUR |  |  |  |  | 0
Grand Total for Lot 2 in EUR |  |  |  |  | 0

## GENERAL REQ
PUBLIC PROCUREMENT CONTRACT FOR SUPPLY AND INSTALLATION OF ROOF-TOP SOLAR PHOTOVOLTAIC SYSTEMS ON SCHOOLS IN GAZA STRIP
TENDER NO. PZA1203211-10026
ANNEX 1 – BILL OF QUANTITIES
GENERAL REQUIREMENTS
· System Type: on-grid connected with battery backup system.
· The Contractor shall submit As-Built drawings for all architectural, civil, electrical and a complete PV solar system works, including a single line diagram showing all the components of the PV system, DC and AC distribution boards, PV Arrays layout and battery backup systems connections and cables, wires’ cross section as per the approval.
· The Contractor shall equip the system room with A3 size As-Built guide drawings for all electrical and a complete PV solar system works, including a single line diagram showing all the components of the PV system, DC and AC distribution boards, PV Arrays lay out and battery backup systems connections and cables, wires’ cross section (This is for maintenance purposes and follow-up).
· The Contractor shall install in the system room warning signs for general and personal safety.
· The Contractor shall submit the product datasheet showing conformance to the requested specifications stated in the bill of quantity.
· The Contractor shall submit the Manufacture testing certificate, country of origin, certified characteristics, test performance curves, and spare parts as recommended by manufacturer, maintenance manuals, and manufacturer’s warranty for each component of the system.
· Upon completion of the installation, the Contractor shall organize an on-site training program involving nominated employer's staff. The training shall be executed for 7 people on operating, programming, and maintaining the system through installation and commissioning process. Such a program shall be carried out during the commissioning phase.
· All DC and AC cables must be sized in accordance with the installation requirements applicable on site and as per the drawings.
· Supply, install and connect all DC and AC cables appropriately sized in accordance with the installation requirements and the drawing in order to connect the inverters with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors to have a complete job, the allowable voltage drop for DC cables between inverters and PV system not to exceed 1%.