## Cover page
Supply, delivery and installation of three (03) generators and construction of three (03) shelters for the Health Training Institutions
2024-04-04

## Summary
Supply, delivery and installation of three generators and construction of shelters for 3 Health Training Institutions
BOQ AMOUNT
Item | Description | Unit | Qty | Rate (EUR) | Amount EUR)
GENERAL SUMMARY
| Preliminary works |  |  |  | 0
| Mail bill |  |  |  | 0
| Sub-Total for 1No. Generator |  |  |  | 0
| Grand Total 3 No. Generator (Vat Exclusive) |  |  |  | 0

## Preliminary
Supply, delivery and installation of three generators and construction of shelters for 3 Health Training Institutions
BOQ QUANTITY
Preliminary works
Item | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
A | Protection of Works from weather | SUM | 1 | 0 | 0
B | Tools, plant and false works | SUM | 1 | 0 | 0
C | Site Supervision | SUM | 1 | 0 | 0
D | Water for the Works | SUM | 1 | 0 | 0
E | Temporary light and Power for the Works | SUM | 1 | 0 | 0
F | Site Security | SUM | 1 | 0 | 0
G | Hoarding around construction sites, where required | SUM | 1 | 0 | 0
H | Removing rubbish and reinstating site | SUM | 1 | 0 | 0
I | Workmen compensation policy | SUM | 1 | 0 | 0
| Total to general summary (VAT EXCL) |  |  |  | 0

## Main Bill
Supply, delivery and installation of three generators and construction of shelters for 3 Health Training Institutions
Main Bill
BOQ QUANTITY
Bill 1: Generator
N° | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
1 | Procurement for supply, installation and commissioning of 1No 60KVA, 3 phase, Diesel Generator. The generator should be silent and have remote monitoring enabled and Data provided monthly or as requested by the client. The exhaust pipe of the generator should be extended at least 1.5m above the roof of the shelter. | No. | 1 | 0 | 0
2 | Supply and install 35mm2 armoured main supply copper cable from power control room to the generator including terminating to board made in Uganda or equivalent. | M | 260 | 0 | 0
3 | Supply and installation three phase 100A manual changeover switch | No | 1 | 0 | 0
4 | Provide and install earthing to the generator comprising of Earth electrodes made from Hard drawn copper or copper weld 2mm diameter by 1200mm in two length screwed together complete with cap, earth clamp, manhole and all accessories inclusive testing and test certificate for less than 10 Ohms. | Item | 1 | 0 | 0
5 | Installation assorted accessories and labour | Item | 1 | 0 | 0
6 | Supply and install 16mm2 4 core armoured copper cable from existing power control room (Genset) to the multi-purpose hall including terminating to board made in Uganda or equivalent. | M | 100 | 0 | 0
7 | Excavate trench for 16mm2 cable not exceeding 1.5m and average width of 300mm from existing Generator house to Multi-purpose hall | M | 200 | 0 | 0
8 | Ditto but for 35mm2 cable to new Generator location near feeder pillar No.1 | M | 130 | 0 | 0
9 | Weather proof Feeder Pillar: 500A TPN 4way, complete with 500A TPN Incomer MCCB;1Nox400A, 3Nox63A, TPN outgoing MCCBs complete with Voltmeter, Ammeters and all accessories as SCHNEIDER ELECTRIC BLOCK SET manufacture or as made by Electrical Controls and Switchgear or equal approved to be located near power house. | No | 1 | 0 | 0
10 | Cutting and re-instatement for builders work in concrete, masonry at generator house and veranda and storm drainage points along cable paths. | Item | 1 | 0 | 0
Total Bill 2 excl. VAT (€): |  |  |  |  | 0
Bill 2: Concrete platforms
N° | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
SUBSTRUCTURE (All Provisional)-3m x2.5m
Excavations
1 | Excavate oversite to remove top soil average 150mm deep and remove from site. | M3 | 1.5 | 0 | 0
2 | Excavate foundation trench not exceeding 1.50 m deep. | M3 | 2 | 0 | 0
3 | 150mm thick brickwork in cement sand mortar mix 1:4 as plith walling | SM | 30 | 0 | 0
4 | Remove excavated material from site | M3 | 1.5 | 0 | 0
5 | Return fill and ram selected excavated material around foundation | M3 | 1 | 0 | 0
6 | 1000 gauge polythene plastic sheeting with 300mm welted lap joints | Sq. | 7.5 | 0 | 0
7 | Murram filling
8 | Murram filling well spread levelled rammed and consolidated in 100mm 'layers' | M3 | 1 | 0 | 0
Plain concrete class 15/20mm Aggregate in:
9 | 50 mm blinding under beams | M3 | 0.5 | 0 | 0
Vibrated reinforced Concrete Class 25/20mm
Aggregate in:
10 | 150 mm thick slab | M3 | 2 | 0 | 0
11 | Cement sand plaster 20mm thick to plinth walling mortar mix 1:3 | SM | 30 | 0 | 0
High Tensile Steel Bar Reinforcement
(Provisional)
12 | 12 mm | Kg | 60 | 0 | 0
13 | 8 mm | Kg | 8 | 0 | 0
14 | Fabric mesh reinforcement BRC mesh ref No. A142 laid in floor slab. | Sq. | 12 | 0 | 0
15 | Supply, fabricate and install 100mmx100mmx10mm steel angle frame with hold down hook bars 150mm placed at 300mm along the frame length and cast in concrete slab/beam complete with hole provision for securing the generator at installation | Lm | 9 | 0 | 0
Sawn Formwork as described to:
16 | Sides of ground beam and slab | Lm | 12 | 0 | 0
Total Bill 3 excl. VAT (€): |  |  |  |  | 0
Bill 3: Shelter frame
Item | Description | Unit | Qty | Unit price excl. VAT (€) | Total price excl. VAT (€)
BILL 4: SHELTER FRAME
PURPOSE MADE STANDARD Steel burglar proofing made from 20 x 20 x 2mm SHS vertical grills everywhere placed at 150mm along the shelter perimeter and 60 x 40x2mm vertical supports at 4 no corner points, 2no door support and 1no mid back side RHS : one coat red oxide primer as per Architect's detailed drawing
A | Cage; size 4200mm x 2700mm x 2400mm high front and 2100mm high on the back; complete with and including 1500 x 2100mm high steel grilled door | Item | 1 | 0 | 0
PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat and two Gloss finishing coats; on metal work : to
B | General steel surfaces | Item | 1 | 0 | 0
ROOF WORKS
Structural Steelwork
The rates for structural steel work should include all plates, stiffeners, bolts, welded joints, all connections and accessories; painting and decorations; as per the architect’s and structural engineer’s drawings; the contractor must study the drawings and ensure that his price includes all items as shown on the drawings
Structural Steelwork : framed : one coat red-oxide primer;
C | 50 x 50 x 2.0mm SHS wall plate for back and front of shelter | Kg | 50 | 0 | 0
D | 50 x 25 x 2.0mm SHS for rafter placed at side, middle and side | Kg | 45 | 0 | 0
E | 50 x 25 x 2.0mm SHS for Purlin placed at top, middle and bottom of roof structure | Kg | 50 | 0 | 0
SUNDRIES
F | Allow for all connections plates, cleats, weld joints and heavy duty bolts, nuts and washers to approval, including all builders work during erection of shelter | Item | 1 | 0 | 0
ROOF COVERING
26 Gauge pre-painted IT4 roofing sheets : fixed to angle purlins with J-bolts : in
G | Sheet laid sloping not exceeding 22.5 degrees from horizontal overall roof cover size 3.5m x 3.0m. | SM | 20 | 0 | 0
H | Allow for supply and installation of all necessary safety and user signage | Item | 1 | 0 | 0
A | STEEL GRILLLLED DOOR detail see below;
PURPOSE MADE GRILLED DOORS: Standard Steel grilled door comprising of: 50 x 50 x 3mm RSA door frame; 40 x 40 x 3mm RHS framing and transoms; all iron-mongery and accessories; one coat red oxide primer; as per Architect's drawing
B | Door size 1500 x 2100mm high (overall) | No | 1 | 0 | 0
| PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat and two Gloss finishing coats; on metal work surfaces | Item | 1 | 0 | 0
C | General door surfaces | Item | 1 | 0 | 0
Total Bill 4 excl. VAT (€): |  |  |  |  | 0
Bill 4 | Provision of 1/2 day user training on site (in 1 Health Training Institute exc. VAT (€): |  |  |  | 0
Bill 5 | Delivery costs to 1 HTI exc. VAT (€): |  |  |  | 0
Total Bill 4 excl. VAT (€): |  |  |  |  | 0