## Aspersao Low
Sprinkler (2.00 ha) | Unit | Quantity | Coments
Pressure gauge 6 bar de 63 mm x 1/4" | ea | 1 | Brand and specs with sketch or pictures. Details and quantities of each fittings. Exclusion of brass/copper/IPS/PPR based material.. Optional certification
Fittings for pressure gauge connection to mainline | bulk | 1
HDPE pipe CL6 Ø90mm | m | 100 | Brand & specs of pipe with pictures, drawing or datasheet and 6 month old max. Brand and details of flushing valves, hydrants and fittings to conect to 63 mm QC pipe. Buried pipe with 50 m space from river, hydrant to be installed on 50 m of Ø90mm, 100 m of Ø75mm and 50 m of Ø63mm pipes. Certification optional
HDPE pipe CL6 Ø75 mm | m | 100
HDPE pipe CL6 Ø63 mm | m | 50
Plastic flushing valve Ø50 mm | bulk | 1
Plastic Hydrant Ø63 mm (ea) | ea | 10
HDPE pipe CL6 x Ø63 mm Quick coupling 6 m | ea | 24 | Brand, pictures, drawings, catalogue of quick coupling pipe & fittings
HDPE pipe CL6 x Ø50 mm Quick coupling 6 m | ea | 24
T Quick coupling Ø50 mm | ea | 2
T Quick coupling Ø63 mm | ea | 1
Elbow Quick coupling Ø50 mm | ea | 2
Elbow Quick coupling Ø63 mm | ea | 1
Reducer Quick coupling Ø63/50 mm | ea | 3
End cap Quick coupling Ø50 mm | ea | 3
Plastic sprinkler 20 mm of 750 lph min @ 1.7 bar max | ea | 30 | Sprinkler wetted Ø 16 m minimum. Spacing 10 m x 10 m. Details of riser pipe connection to QC pipes. manufacturer specs. Certification optional
Plastic riser of 20 mm x 1 m | ea | 30
Distribution system fittings | bulk | 1 | Includes 2 direction hydrants and quick coupling fittings for lateral. Brand, quantities and details of each fittings for complete installation of 3 QC lateral. Details of easy and flexible connection of pump to mainline. Exclusion of brass/copper/IPS/PPR based material. Certification optional. manufacturer datasheet or catalogue required
Complete direct surface solar pump 150 m³/day @ 25 m delivery head/solar submersible pump 150 m³/day @ 30 m. Consider min hourly flow of 22.5 m³ for 30 sprinklers. Suction and deliver pipe Ø and length, connection details between pump and mainline. Duty point at 15% max from BEP (Y=X-0.15*X), Y = selected duty point and X=BEP | bulk | 1 | Drawings, sketch of pump house/controller/inverter (water source ΔH 5 m max and 5 m max horizontal distance). Cross section size and length power cable from pump to controller/inverter (3% voltage drop). Brand of solar pump, pump curves and monthly/daily volume produced at required head. Pump flow measurement solution datasheet. Cables specs required. Mandatory certification
Solar panels de 550 Wp & 20% eff. min e controller/inverter connection accessories | bulk | 1 | Drawings, sketch , pictures of solar panels anti theft support structure. Consider 30 m max apart from controller/inverter. Cross section size and length power cable from pump to controller/inverter (3% voltage drop). Certification mandory for cable and optional for support structure. Manufacturer specs or datasheet
Material for suction and delivery pipe | bulk | 1 | Length and Ø of suction and delivery pipe. Details of fittings
Transport, Installation and performance tests | bulk | 1 | SPIS operation and maintenance training manual (minimum table of contents) for producers & extension workers.
Total for each SPIS

## resumo antigo (hidden)
|  | até 100 m | contribuição | até 200 m | contribuição | Até 300 m | contribuição | Até 400 m | contribuição | até 500 m | contribuição | Hypothese de calculo
Gravidade | 0,25 ha | 150000 | 30000 | 165000 | 33000 | 185000 | 37000 | 205000 | 41000 | 225000 | 45000
| 0,5 ha | 175000 | 35000 | 190000 | 38000 | 207500 | 41500 | 227500 | 45500 | 245000 | 49000
| 1 ha | 796500 | 159300 | 840000 | 168000 | 896000 | 179200 | 953000 | 190600 | 1010000 | 202000
| 2 ha | 955000 | 191000 | 990000 | 198000 | 1040000 | 208000 | 1090000 | 218000 | 1140000 | 228000
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Aspersão | 0,25 ha | 155000 | 31000 | 170000 | 34000 | 195000 | 39000 | 217500 | 43500 | 240000 | 48000
| 0,5 ha | 184000 | 36800 | 200000 | 40000 | 220000 | 44000 | 240000 | 48000 | 260000 | 52000
| 1 ha | 707500 | 141500 | 765000 | 153000 | 840000 | 168000 | 915000 | 183000 | 990000 | 198000 | fonte de agua a 100 m requer 200 m de PEBD 100 mm x CL3 ;depois, + 100m deste para cada 100m adicional na distancia; outros tubos segundo proporçao inicial.
| 2 ha | 1235000 | 247000 | 1355000 | 271000 | 1480000 | 296000 | 1600000 | 320000 | 1725000 | 345000 | fonte de agua a 100 m requer 200 m de PEBD 100 mm x CL3 ;depois, + 100m deste para cada 100m adicional na distancia; outros tubos segundo proporçao inicial.
0
0