## Cover
WECARE
Public Works Contract for Wiring Modifications and Installation of a Switch Station at Rukoki HCIV, Kasese District
2025-04-08

## Rukoki Summary
Summary |  | 1/3
Item | Description | Amount (Euro excl. VAT)
1 | Preliminary works | 0
2 | Mail bill | 0
| Total Excl. VAT | 0

## Rukoki Preliminaries
Preliminaries |  | 2/3
Item | Description | Amount (Euro excl. VAT)
A | Site mobilisation
Allowance for safety on site, welfare, scaffoldings and transport
B | Protection
The Contractor shall cover up and protect from damage, including damage from inclement weather, all finished work and unfixed materials including that of the Sub-Contractor, etc., to the satisfaction of the Project Manager until the completion of the Contract and make good any damage which occurs.
C | Removal of plant, Rubbish, etc
The Contractor shall, upon completion of the Works, remove and clear away all rubbish and unused material, and shall leave the whole of the Site of the Works in a clean and tidy state to the satisfaction of the Project Manager. He shall also remove all rubbish and dirt from the Site at weekly intervals or as directed by the Project Manager. Particular care shall be taken in leaving windows clean and removal of any stains therefrom.
D | Prevention of Nuisance
The Works and such sections of the Site necessary therefore shall be under the entire care and control of the Contractor during the whole period of the Contract and he shall take all possible precautions to prevent any nuisance, inconvenience or injury to the holders or occupiers of the existing or surrounding properties and to the public generally, and shall at all times keep all the paths and walkways affected by the works in a safe and clear state and shall use proper precautions to ensure the safety of all wheeled traffic and pedestrians.
E | Visitors to the site
The Contractor is required to control all visitors to the Site and to keep out unauthorised visitors and to provide a visitors book and ensure that all the authorised visitors sign therein.
F | Contractor's Project and Site Administration; and Foreman-in-charge
The Contractor shall permanently deploy the Project and Site Administrative Staff approved by the Contract administrator. These will include a General Foreman-in-charge and other trades foremen properly qualified and fluent in English. The Contractor shall submit a Site Organization Structure Chart within seven (7) days of commencement of the Contract.
| TOTAL CARRIED TO SUMMARY | 0

## Rukoki Main Bill
Main Bill |  |  |  |  | 3/3
Item | Description | Unit | Qty | Rate (Euro) | Amount (Euro)
1 | Electrical Panel Concrete Platform
Site Preparation
1.1 | Clear site of bush and under grouth, cut down and clear away small trees not exceeding 300mm girth, grub up roots | m2 | 15 |  | 0
Excavation and Earthworks.
Note: Rates for excavation to include for keeping excavations free from water and planking and strutting to sides of excavations
1.2 | Excavate oversite to reduce levels | m3 | 1 |  | 0
1.3 | Excavate pit/strip for pads foundations: commencing from reduced levels: not exceeding 1.5m deep . | m3 | 2 |  | 0
Disposal of excavated material
1.4 | Return, fill and ram selected excavated materials around foundations in 150mm layers and compact to 98% MDD. | m3 | 2 |  | 0
Reinforcement works
1.5 | 12mm diameter bar | Kg | 70 |  | 0
1.6 | 8mm diameter bar | Kg | 20 |  | 0
1.7 | Form work to sides of stab foooting | SM | 6 |  | 0
Insitu concrete class25/ 20mm aggregate as described.
1.8 | Stab footing | m3 | 1 |  | 0
1.9 | 450x 450x75mm thick precast concrete reinofrced slabs, slabs reinforced with A98 BRC mesh, laid on compacted imported murram, on 50mm thick sand bedding including filling joint swith cement and sand mortar 1:3 | m2 | 4 |  | 0
Kerb stones
1.1 | 125mm x 300mmx 900mm Half-battered kerbs to BS 340 bedded and jointed in cement sand (1:3) mortar on and including 450mm x 200mm thick concrete grade 20 bed and 100mm hauching at back including all necessary excavation and formwork | LM | 10 |  | 0
Sundries
1.11 | Approved marrum fill to make up levels; well rolled and compacted to 95% MDD to Engineer's approval | m3 | 1 |  | 0
| Total Electrical Panel Concrete Platform carried to collection |  |  |  | 0
Item | Description | Unit | Qty | Rate (UGX) | Amount (UGX)
2 | Supply and Install to the satisfaction of the contracting Engineer a 3-cubicle box type outdoor switch station complete with all accessories
2.1 | Mains Incomer MCCB 315A, 4P, Adjustable Thermal Setting | No | 1 |  | 0
2.2 | DG Incomer MCCB 125A, 4P, Adjustable Thermal Setting | No | 1 |  | 0
2.3 | Busbar System: 4 Copper Bars, 400A, 1.4m each, complete with phase separators, insulated mounting supports, bolts & fastners, and busbar clamps | Set | 1 |  | 0
2.4 | Outgoing MCCB: 160A, 4P with fuse | No | 1 |  | 0
2.5 | Outgoing MCCB: 125A, 4P with fuse | No | 2 |  | 0
2.6 | Outgoing MCCB: 63A, 4P with fuse | No | 2 |  | 0
2.7 | Main incomer cable 4-Core, 95mm² copper amoured cable | m | 20 |  | 0
2.8 | Outgoing cable 4-Core, 70mm² copper amoured cable | m | 150 |  | 0
2.9 | Outgoing cable 4-Core, 70mm² copper ABC cable | m | 50 |  | 0
2.1 | Excavate trench for 70mm2 cable not exceeding 1.5m and average width of 300mm including backfilling | m | 150 |  | 0
2.11 | Earthing system complete with an inspection chamber and all accessories | Item | 1 |  | 0
2.12 | Surge protection device: Type 1 SPD, 100 kA Imax, 400V | No | 1 |  | 0
2.13 | Surge protection device: Type 2 SPD, 40 kA Imax, 400V | No | 1 |  | 0
2.14 | 3-Phase digital multimeter | No | 1 |  | 0
2.15 | Manual Change over 400A, 4P | No | 1 |  | 0
2.16 | Panel enclosure IP54-rated box type enclosure/panel (L=2.5m x W= 0.5m x H=1.8m) with 3 cubicles (L=0.75m x W= 0.5mx H=1.7m) complete with door shutters, insulated covers, and other accessories | No | 1 |  | 0
| Total switch station carried to collection |  |  |  | 0
Item | Description | Unit | Qty | Rate (UGX) | Amount (UGX)
3 | Modify Electrical Wirigs and Install to the satisfaction of the supervising Engineer, the following existing buildings
Theatre - 3Ph upgrade
3.1 | 125A 3P MCCB | No | 1 |  | 0
3.2 | 6Way 3ph distribution board-100A Hager or equal approved | No | 1 |  | 0
3.3 | 16mm2 4-core copper armoured cable | m | 25 |  | 0
3.4 | 10mm2 4-core copper cable | m | 25 |  | 0
3.5 | 3ph socket outlets c/w accessories | No | 3 |  | 0
3.6 | 3P Surface Mounted 32A-Fused Isolator Switch, Eaton or equal approved | No | 3 |  | 0
3.7 | Double sockets complete with MK boxes and screws | No | 8 |  | 0
3.8 | 2.5mm2 twin cable | m | 20 |  | 0
3.9 | PVC trunking-100x100 mm | m | 25 |  | 0
Old MCH - 3Ph upgrade
3.1 | 125A 3P MCCB | No | 1 |  | 0
3.11 | 6Way 3ph distribution board-100A Hager or equal approved | No | 1 |  | 0
3.12 | Load Cable 16mm2 4-core copper armoured cable | m | 25 |  | 0
3.13 | 10mm2 4-core copper cable | m | 25 |  | 0
3.14 | 3ph socket outlets complete with accessories | No | 3 |  | 0
3.15 | 3P Surface Mounted 32A-Fused Isolator Switch, Eaton or equal approved | No | 2 |  | 0
3.16 | Double sockets complete with MK boxes and screws | No | 8 |  | 0
3.17 | 2.5mm2 twin cable | m | 20 |  | 0
3.18 | PVC trunking-100x100 mm | m | 25 |  | 0
NICU-3ph upgrade + Sockets+Lights
3.19 | 125A 3P MCB | No | 1 |  | 0
3.2 | 4Way 3ph distribution board-100A Hager or equal approved | No | 1 |  | 0
3.21 | Load Cable 16mm2 4-core copper armoured cable | m | 25 |  | 0
3.22 | 10mm2 4-core copper | m | 25 |  | 0
3.23 | 3ph socket outlets complete with accessories | No | 3 |  | 0
3.24 | 3P Surface Mounted 32A-Fused Isolator Switch, Eaton or equal approved | No | 2 |  | 0
3.25 | Double sockets complete with MK boxes and screws | No | 8 |  | 0
3.26 | 2.5mm2 cable twin | m | 20 |  | 0
3.27 | LED light tubes c/w fittings | No | 5 |  | 0
3.28 | 2.5mm2 twin cable | m | 20 |  | 0
3.29 | 1.5mm2 twin cable | m | 20 |  | 0
3.3 | PVC trunking-100x100 mm | m | 25 |  | 0
3.31 | PVC Trunking 25x25mm | m | 20 |  | 0
Family Planning-Terminal box and MCB for Proper Insolation
3.32 | 125A 1P MCB | No | 1 |  | 0
3.32 | Load Cable 16mm2 4-core copper armoured cable | m | 15 |  | 0
3.33 | Metal box | No | 1 |  | 0
3.34 | 4Way distribution board | No | 1 |  | 0
| Total Electrical Modifications carried to collection |  |  |  | 0
Item | Description | Unit | Qty | Rate (UGX) | Amount (UGX)
COLLECTION
| Page 1 |  |  |  | 0
| Page 2 |  |  |  | 0
| Page 3 |  |  |  | 0
| Grand Total Carried to Summary |  |  |  | 0