## Cover_page
WECARE
Public Works Contract for Solar System Installation at Nyamirami HCIV Lab and Maternity Blocks, Kasese District
2025-04-05

## Summary
Summary |  | 1/4
Item | Description | Amount (Eur excl. VAT)
1 | Preliminary works | 0
2 | Main Bill-Lab | 0
3 | Main Bill-Maternity and NICU | 0
| Sub-total | 0
| Add 5% contigency | 0
| Total Excl. VAT | 0

## Preliminaries
Preliminaries |  | 2/4
Item | Description | Amount (Euro excl. VAT)
A | Site mobilisation
Allowance for safety on site, welfare, scaffoldings and transport
B | Protection
The Contractor shall cover up and protect from damage, including damage from inclement weather, all finished work and unfixed materials including that of the Sub-Contractor, etc., to the satisfaction of the Project Manager until the completion of the Contract and make good any damage which occurs.
C | Removal of plant, Rubbish, etc
The Contractor shall, upon completion of the Works, remove and clear away all rubbish and unused material, and shall leave the whole of the Site of the Works in a clean and tidy state to the satisfaction of the Project Manager. He shall also remove all rubbish and dirt from the Site at weekly intervals or as directed by the Project Manager. Particular care shall be taken in leaving windows clean and removal of any stains therefrom.
D | Prevention of Nuisance
The Works and such sections of the Site necessary therefore shall be under the entire care and control of the Contractor during the whole period of the Contract and he shall take all possible precautions to prevent any nuisance, inconvenience or injury to the holders or occupiers of the existing or surrounding properties and to the public generally, and shall at all times keep all the paths and walkways affected by the works in a safe and clear state and shall use proper precautions to ensure the safety of all wheeled traffic and pedestrians.
E | Contractor's Project and Site Administration; and Foreman-in-charge
The Contractor shall permanently deploy the Project and Site Administrative Staff approved by the Contract administrator. These will include a General Foreman-in-charge and other trades foremen properly qualified and fluent in English. The Contractor shall submit a Site Organization Structure Chart within seven (7) days of commencement of the Contract.
| TOTAL CARRIED TO SUMMARY | 0

## Main Bill-Lab
Mail bill - Lab |  |  |  |  | 3/4
Item | Description | Unit | Qty | Rate (EUR) | Amount (EUR)
A | Solar system
A.1 | 580W solar panel | pcs | 12 |  | 0
A.2 | PV Solar cable 4mm² with the MC4-male and female connectors properly crimped. Cable used to connect PV panels in series | m | 40 |  | 0
A.3 | PV Solar cable 6mm² with the MC4-male and female connectors properly crimped to connect PV panels in parallel up to the combiner box | m | 20 |  | 0
A.4 | 6mm² armoured cable for collecting the panel circuits from the adjacent Theatre building to the combiner box installed in the Maternity block | m | 15 |  | 0
A.5 | Excavate trench for the 6mm² armoured cable connecting between the Lab and OPD blocks including backfilling | m | 12 |  | 0
A.4 | Combiner box 300x300x120mm for collecting battery and PV circuits | pcs | 1 |  | 0
A.5 | Cable 6mm² from the combiner box to hybrid inverter | m | 5 |  | 0
A.6 | Supply and install Surge Protection Device (type 2) for both AC and DC ciruits | pcs | 2 |  | 0
A.7 | Supply and install a hybrid inverter with in-built MPPT controller of AC output power of 5kVA and PV input power of 7kW or equal approved combination of a hybrid inverter and additional standalone MPPT controller capable of PV input power of 7kW. See technical specifications attached as annex the inverter must conform to. | pcs | 1 |  | 0
A.8 | 51.2V, 200Ah, lifetime of 6000 cycles at 80% depth of Discharge at 25°C. Such as Eastman ES51.2-200LP or equal approved | pcs | 6 |  | 0
A.9 | 6mm² cable for interconnecting batteries | m | 10 |  | 0
A.10 | Battery cable of 10mm² to collect the battery bank to the combiner box and to the inverter | m | 5 |  | 0
A.11 | DC breaker for battery system | pcs | 1 |  | 0
A.12 | Lockable steel battery cabinet of dimensions 1.5mx1.0mx1m to store 8 batteries, covered with 1.2 mm mild steel plates on all side with air vents and lockable door at the front. | Item | 1 |  | 0
A.13 | Trunking of 50x50mm, PVC white, with removable cover, to conceal cables from inverter to batteries and from panels | m | 20 |  | 0
A.14 | 4way Distribution Board | pcs | 1 |  | 0
A.15 | Installation assorted accessories including junction boxes, strip connectors 60A, clips, insulating tape, cable lugs, screws, nuts, rubber covers, and copper bar strips, etc. | Item | 1 |  | 0
B | Solar panel support structure Assuming a panel size of (3mx1.1m), 12 solar panels will be mounted on the existing roofs of the Lab block and adjacent OPD block. Solar panel steel supporting structure mounted on the roof, complete with anti-thefty lock, brackets, and accessories, minimum 40x40mm sections including fixing the panels by riveting onto the support strucuture primed and painted against rust and corrosion
B.1 | Steel solar panel structure | kg | 100 |  | 0
| Sub_Total |  |  |  | 0
C | Visual information & knowledge management The following items will be supplied and/installed for the purpose of Maintenance and Operations of the installed systems
C.1 | Operational manual; Comprehensive Operation and Maintenance manual for the installed system, written in English and graphically illustrated for unambiguous interpretation and understanding by Operation and Maintenance staff. Special attention shall be drawn to fault finding and remedial action. The manual shall include a system wiring diagram, a list of spare parts and the names of the accredited suppliers/agents of these spare parts. The manual shall also include the manufacturer's name, model number, service manuals, parts list and brief descriptions of all equipment and their basic operating features i.e. routine maintenance procedures, possible breakdowns and repairs, recommended spare parts, troubleshooting guide, equipment layout and simplified wiring and control diagrams of the system as installed. | pcs | 1 |  | 0
C.2 | Component signage; each component of the installed systems should be clearly labelled onto sticker paper or equal/better approved material and securely mounted directly adjacent to the component. The lettering shall be high contrast and no less than 50mm and no more than 75mm in size. Sites where only specific components are being replaced will be treated similarly to sites where full installations will be done; i.e. labels will also be installed against all existing components of systems where the contractor only replaces certain parts. | Ls | 1 |  | 0
C.3 | System chart/layout; an A1 size chart showing the entire system with its parts and wiring, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 |  | 0
C.4 | Error/warning chart; an A1 size chart illustrating common warning signs and error messages, and their meanings, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 |  | 0
| Sub_Total |  |  |  | 0
D | Lightning and Earthing for the Theatre block All materials to be supplied and installed, compliant with the IEC 62305 and NFC 21-201 standards, to obtain at most 10ohms earth resistance. All termination points to be properly done.
D.1 | 16mm(D)*1000mm(L) air terminal | pcs | 1 |  | 0
D.2 | HO5 V/K flexible copper cable 16mm2 for all equipotential bonding and earthing, compliant with the IEC 62305 and NFC 21-201 standards | m | 15 |  | 0
D.3 | 3mm*25mm copper tape hard drawn complete with saddles. | m | 10 |  | 0
D.4 | Supply and install 600mmx600m earthing mat at a depth of at least 0.5m | pcs | 1 |  | 0
D.5 | Precast Inspection chamber of 300mmx300mm complete with cover made of grade 25 concrete | m3 | 0.05 |  | 0
D.6 | Excavate pit 1000 x 1000 x 500 mm (L x W x D) and place course salt mixed with charcoal dust and soil in pit and compact and the earthing mat into this pit, connect and place precast manhole 300 x 300 complete with cover marked with earth symbol. | pcs | 1 |  | 0
D.7 | Allow for installation accessories such a s connectors | Item | 1 |  | 0
D.8 | 32mm diameter PVC pipe well clipped to the external walls to conceal the conductor to a height of 3m | m | 10 |  | 0
E | Lightning and Earthing Adaptation to the existing system, Earth resistance <10 Ohms. All termination points to be properly done.
E.1 | HO5 V/K flexible copper cable 16mm2 for all equipotential bonding and earthing, compliant with the IEC 62305 and NFC 21-201 standards | m | 30 |  | 0
E.2 | 25mm diameter PVC conduit well clipped to conceal the cable | m | 10 |  | 0
| Sub_Total |  |  |  | 0
F | Adaptation of electrical system of the building for solar system. This includes the adaptation of existing board, installation of new wires and sockets.
F.1 | Switches and lights complete with accessories including wiring by 1.5mm² copper cable concealed in 25x25mm trunking. | pcs | 3 |  | 0
F.2 | Double sockets complete with all accessories to be wired by 2.5mm² copper cable and concealed in 25x25mm trunking | pcs | 4 |  | 0
| Sub_Total |  |  |  | 0
| Grand Total(Vat Exclusive) |  |  |  | 0

## Main Bill-Maternity and NICU
Mail bill - Maternity and NICU |  |  |  |  | 4/4
Item | Description | Unit | Qty | Rate (EUR) | Amount (EUR)
A | Solar system
A.1 | 580W solar panel | pcs | 50 |  | 0
A.2 | PV Solar cable 4mm² with the MC4-male and female connectors properly crimped to interconnect the panels | m | 80 |  | 0
A.3 | PV Solar cable 6mm² with the MC4-male and female connectors properly crimped to collect the panel circuits up to the combiner box | m | 50 |  | 0
A.4 | 6mm² armoured cable for collecting the panel circuits from the adjacent Theatre building to the combiner box installed in the Maternity block | m | 30 |  | 0
A.5 | Excavate trench for the 6mm² armoured cable connecting between the Theatre and Maternity blocks including backfilling | m | 20 |  | 0
A.6 | Combiner box 300x300x120mm for collecting battery and PV circuits | pcs | 1 |  | 0
A.7 | Cable 6mm² from the combiner box to hybrid inverter | m | 10 |  | 0
A.8 | Supply and install Surge Protection Device (type 2) for both AC and DC ciruits | pcs | 2 |  | 0
A.9 | Supply and install a hybrid inverter with in-built MPPT controller of AC output power of 16kVA and PV input power of 29kW or equal approved combination of a hybrid inverter and additional standalone MPPT controller capable of PV input power of 29kW. See technical specifications attached as annex the inverter must conform to. | pcs | 1 |  | 0
A.10 | 51.2V, 200Ah, lifetime of 6000 cycles at 80% depth of Discharge at 25°C. Such as Eastman ES51.2-200LP or equal approved | pcs | 10 |  | 0
A.11 | 6mm² cable for interconnecting batteries | m | 15 |  | 0
A.12 | Battery cable of 10mm² to collect the battery bank to the combiner box and to the inverter | m | 10 |  | 0
A.13 | DC breaker for battery system | pcs | 2 |  | 0
A.14 | Lockable steel battery cabinet of dimensions 2.0mx1.0mx1.5m to store 8 batteries, covered with 1.2 mm mild steel plates on all side with air vents and lockable door at the front. | Item | 1 |  | 0
A.15 | Trunking of 50x50mm, PVC white, with removable cover, to conceal all surface run cables from inverter to batteries and from panels | m | 40 |  | 0
A.16 | 6way Distribution Board | pcs | 1 |  | 0
A.17 | Installation assorted accessories including junction boxes, strip connectors 60A, clips, insulating tape, cable lugs, screws, nuts, rubber covers, and copper bar strips, etc. | Item | 1 |  | 0
A.18 | Modular single-phase energy meter Victron/Schneider or equal approved | pcs | 1 |  | 0
B | Solar panel support structure Assuming a panel size of (3mx1.1m), 50 solar panels will be mounted on the existing roofs of the Maternity block and adjacent Theatre block. Solar panel steel supporting structure mounted on the roof, complete with anti-thefty lock, brackets, and accessories, minimum 40x40mm sections including fixing the panels by riveting onto the support strucuture primed and painted against rust and corrosion
B.1 | Steel solar panel structure | kg | 360 |  | 0
| Sub_Total |  |  |  | 0
C | Visual information & knowledge management The following items will be supplied and/installed for the purpose of Maintenance and Operations of the installed systems
C.1 | Operational manual; Comprehensive Operation and Maintenance manual for the installed system, written in English and graphically illustrated for unambiguous interpretation and understanding by Operation and Maintenance staff. Special attention shall be drawn to fault finding and remedial action. The manual shall include a system wiring diagram, a list of spare parts and the names of the accredited suppliers/agents of these spare parts. The manual shall also include the manufacturer's name, model number, service manuals, parts list and brief descriptions of all equipment and their basic operating features i.e. routine maintenance procedures, possible breakdowns and repairs, recommended spare parts, troubleshooting guide, equipment layout and simplified wiring and control diagrams of the system as installed. | pcs | 1 |  | 0
C.2 | Component signage; each component of the installed systems should be clearly labelled onto sticker paper or equal/better approved material and securely mounted directly adjacent to the component. The lettering shall be high contrast and no less than 50mm and no more than 75mm in size. Sites where only specific components are being replaced will be treated similarly to sites where full installations will be done; i.e. labels will also be installed against all existing components of systems where the contractor only replaces certain parts. | Ls | 1 |  | 0
C.3 | System chart/layout; an A1 size chart showing the entire system with its parts and wiring, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 |  | 0
C.4 | Error/warning chart; an A1 size chart illustrating common warning signs and error messages, and their meanings, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 |  | 0
| Sub_Total |  |  |  | 0
D | Lightning and Earthing for the Theatre block All materials to be supplied and installed, compliant with the IEC 62305 and NFC 21-201 standards, to obtain at most 10ohms earth resistance. All termination points to be properly done.
D.1 | 16mm(D)*1000mm(L) air terminal | pcs | 2 | 40 | 80
D.2 | HO5 V/K flexible copper cable 16mm2 for all equipotential bonding and earthing, compliant with the IEC 62305 and NFC 21-201 standards | m | 30 | 3 | 90
D.3 | 3mm*25mm copper tape hard drawn complete with saddles. | m | 25 | 13 | 325
D.4 | Supply and install 600mmx600m earthing mat at a depth of at least 0.5m | pcs | 2 | 72 | 144
D.5 | Precast Inspection chamber of 300mmx300mm complete with cover made of grade 25 concrete | m3 | 0.05 |  | 0
D.6 | Excavate pit 1000 x 1000 x 500 mm (L x W x D) and place course salt mixed with charcoal dust and soil in pit and compact and the earthing mat into this pit, connect and place precast manhole 300 x 300 complete with cover marked with earth symbol. | pcs | 2 |  | 0
D.7 | Allow for installation accessories such a s connectors | Item | 1 |  | 0
D.8 | 32mm diameter PVC pipe well clipped to the external walls to conceal the conductor to a height of 3m | m | 20 |  | 0
E | Lightning and Earthing Adaptation to the existing system at the maternity, Earth resistance <10 Ohms. All termination points to be properly done.
E.1 | HO5 V/K flexible copper cable 16mm2 for all equipotential bonding and earthing, compliant with the IEC 62305 and NFC 21-201 standards | m | 30 |  | 0
E.2 | 25mm diameter PVC conduit well clipped to conceal the cable | m | 15 |  | 0
| Sub_Total |  |  |  | 0
F | Adaptation of electrical system of the building for solar system. This includes the adaptation of existing board, installation of new wires and sockets.
F.1 | Switches and lights complete with accessories including wiring by 1.5mm² copper cable concealed in 25x25mm trunking. | pcs | 5 |  | 0
F.2 | Double sockets complete with all accessories to be wired by 2.5mm² copper cable and concealed in 25x25mm trunking | pcs | 5 |  | 0
| Sub_Total |  |  |  | 0
| Grand Total(Vat Exclusive) |  |  |  | 0