## Technical specifications
Component | Specification Required | Specification Offered | Picture where applicable | Notes
Lot 1
Enclosure/ Outdoor box-type panel | IP54-rated for outdoor use, corrosion-resistant for durability.
Diamensions: L = 2.5m, W = 0.5m, H = 1.8m (with cubicle sections L = 0.75m, W = 0.5m, H = 1.8m)
Insulated Transparent Cover with cut-outs for CB knobs. The cover should flash with the CB knobs to allow operation without removing the cover
Outdoor protective shutters, lockable and weatherproof to protect against rain and dust.
Gasket-sealed for enhanced environmental protection.
Ventilation louvers with filters to prevent moisture build-up while ensuring heat dissipation
Busbar Connection | Insulated mounting supports to ensure proper spacing and mechanical stability
Phase separators to prevent line to line short circuits
Use of clamps for connecting the outgoing MCCBs
Lot 2
16kVA Hybrid Inverter or equal approved combination of a hybrid inverter and additional standalone MPPT controller | Max. PV Input Power 29000W or more
Max. PV Open Circuit Voltage 500V or more
Max. PV Input short circuit current 100A or more
In-built MPPT controller, atleast 1 tracker
Maximum efficiency > 95 %
Internal short circuit protection, overload protection, battery voltage too high, battery voltage too low, temperature too high, input voltage out of range, reverse polarity protection
Charger priority
Output source (Loading) priority
5KVA Hybrid Inverter or equal approved combination of a hybrid inverter and additional standalone MPPT controller | Max. PV Input Power 7000W
Max. PV Open Circuit Voltage 300V or more
Max. PV Input short circuit current >40A
In-built MPPT controller, atleast 1 tracker
Maximum efficiency > 95 %
Internal short circuit protection, overload protection, battery voltage too high, battery voltage too low, temperature too high, input voltage out of range, reverse polarity protection
Charger priority
Output source (Loading) priority
Solar panel | Lifetime of at least 25 years
Conform to CEI 61215 and CEI 61730-1-2
Warranty of min 90% of power after 10 years and 80% at 25 years
Aluminium frame
Battery | Lifetime of 6000 cycles at 80% depth of Discharge at ambiant tempearture
Li-ion battery module
Battery Bank | The prospective bidder shall propose the choice of the bank including the bus voltage for the review and approval by the contracting authority
PV Array | The prospective bidder shall propose a design for the review and approval by the contracting authority
Lot 4
45kVA/36kW generator | 1No. 45kVA/36kW Prime Power 0.8 PF, 3 Phase, 415 Volts, 50 Hz at 1500 RPM.
Engine and alternator model; Europe/USA make or equal approved; Water Cooled.
Control Panel: Integrated Control Panel
Sealed service free dry battery with Leads
80-150 Ltrs inbuilt fuel tank capacity
Soundproof Canopy with less than 70 decibels noise level at 7m.
Changeover switch | Manual changeover switch with rotary control Europe /USA make or equal approved
Functionality: On load changeover between two sources, emergency breaking, selection between two loads, safe isolation of downstream loads for maintenance purpose.
Two earthing external points, wall mounted with 4 bolts, door locking system allows opening ONLY in OFF position, incoming & out going easily interchangeable at site, epoxy polyester powder coated with at least 70 micron and door with solid hinges.
NB | 1. The prospective bidder MUST accompany the specifications schedule with the data sheets/catalogues of the equipment being offered