## Cover Page
THE REPUBLIC OF UGANDA
MINISTRY OF HEALTH
Bidding Document
for the
Procurement of Works
PRICED BILLS OF QUANTITIES
Subject of Procurement: | MINOR WORKS AT BUGEMBE AND MPUMUDDE HEALTH CENTRE IVS- JINJA
Procurement Ref No.:
Date of Submission: | 30TH JULY, 2025

## Main Summary
MAIN SUMMARY |  |  | M/S
MINOR WORKS AT BUGEMBE AND MPUMUDDE HEALTH CENTRE IVS-JINJA
BILL NO. | DESCRIPTION | PAGE NO. |  | AMOUNT (Euro €)
1 | BILL 1 PRELIMINARIES | 1.1 |  | 0
2 | BILL 2 (NICU BLOCK REPAIR WORKS) | 2.1 |  | 0
3 | BILL 3 KITCHEN BLOCK | 3.1 |  | 0
4 | BILL 4 WALK WAY CONSTRUCTION | 4.1 |  | 0
5 | BILL 5 PWD TOILET | 5.1 |  | 0
6 | BILL 6 OXYGEN PIPING | 6.1 |  | 0
7 | BILL 7 SOLAR HOT WATER SYTEM | 7.1 |  | 0
8 | MPUMUDDE MINOR WORKS |  |  | 0
| SUB-TOTAL |  |  | 0
| ADD: CONTINGENCIES | 5% |  | 0
| SUB-TOTAL |  |  | 0
| TOTAL TO AMOUNT EXCLUSIVE OF VAT |  |  | 0
M/S

## Smry. Bl. 1 Prelims
Item |  |  | Description |  | Euro €
BILL No 1
PRELIMINARIES
SUMMARY
|  |  | Total Carried From Page 2/1 |  | 0
|  |  | Total Carried From Page 2/2 |  | 0
|  |  | Total Carried From Page 2/3 | 0 | 0
|  |  | Total Carried From Page 2/4 |  | 0
| 6 |  | Total Carried From Page 2/5 |  | 0
| 7 |  | Total Carried From Page 2/6 |  | 0
| 8 |  | Total Carried From Page 2/7 |  | 0
|  |  | Total Carried From Page 2/8 |  | 0
|  |  | Total Carried From Page 2/9 |  | 0
| 6 |  | Total Carried From Page 2/10 |  | 0
| 7 |  | Total Carried From Page 2/11 |  | 0
|  |  | Total Carried From Page 2/12 |  | 0
8
|  | TOTAL FOR BILL No 2 CARRIED TO MAIN SUMMARY |  |  | 0
PRELIMINARIES | [5 empty] | 1/S

## Bl No.1 Preliminaries.
Item | Description |  |  |  | Euro €
BILL No. 1
PRELIMINARIES
A | Sufficiency of Tender
The Contractor shall be deemed to have satisfied himself before tendering as to the correctness and sufficiency of his Tender for the Works and of the rates and prices stated in the bills of Quantities which rates and prices shall cover all his obligations under the Contract and all matters and things necessary for the proper completion and maintenance of the works
B | Definition of Terms and Abbreviations
The Terms and Abbreviations used in these Tender Documents Shall be interpreted as follows:-
| “ B.S.” |  | shall mean | The current British Standard of Specification published by the British Standard Institution, Park Street, London, W.1 England
| “ NO.” |  | shall mean | Number
| "L.M." |  | shall mean | Linear Meter
| "M" |  | shall mean | Linear Meter
| "SM" |  | shall mean | Square Meter
| "CM" |  | shall mean | Cubic Meter
| "Ditto" |  | shall mean | The whole of the preceding description except as qualified in the section in which it occurs. Where it occurs in brackets, it shall mean the whole of the preceding description which is contained within the appropriate.
| "MS" |  | shall mean | Measured separately
| "BSM" |  | shall mean | Both sides measured
| "P.C" |  | shall mean | Prime cost
| "75mm to 150mm" |  | shall mean | Exceeding 75mm but not exceeding 150mm in girth, and all items described in this manner shall be similarly construed.
| PRELIMINARIES |  |  |  |  | 1/1
A | Access to site and temporary roads
Means of access to the Site shall be agreed with the Project Manager prior to the commencement of the Works and the Contractor must allow for building any temporary access roads for the transport of materials, plant and workmen as may be required for the complete execution of the Works including the provision of temporary culverts, crossings, bridges or any other means of gaining access.
Upon the completion of the Works, the Contractor shall remove such temporary roads, culverts, bridges, etc., and make good and reinstate all Works and services disturbed to the satisfaction of the Project Manager.
B | Area to be occupied by the Contractor
The area of the Site which may be occupied by the Contractor for use as storage and for the purpose of erecting workshops, etc., shall be defined on the Site by the Project Manager.
C | Setting out
The Contractor shall set out the Works in accordance with the dimension and levels shown on the Drawings and shall be responsible for the correctness of all dimensions and levels so set out by him and will be required to amend all errors arising from inaccurate setting out at his own cost and expense. In the event of any error or discrepancy in the dimensions or levels marked on the Drawings being discovered, such errors or discrepancies shall be reported by the Contractor to the Project Manager for his immediate attention.
No Work shall be commenced by the Contractor until he has received written instruction from the Project Manager to adjust such discrepancies which may be proved. Upon receipt of such instructions, the Contractor shall thereupon be responsible for accurate setting out of the Works, giving effect to the adjustments necessary to comply with such instructions, and no claim for extra expense or relief from the provision of the Conditions of Contract and Contract Data based on any discrepancy or error in the dimensions or levels shown on the Drawings may be made thereafter.
Before any Work is commenced by the Sub-Contractors or Specialized Firms, dimensions must be checked on the Site and / or buildings and agreed with the Contractor, irrespective of the comparative dimensions shown on the Drawings. The Contractor shall be responsible for the accuracy of such dimensions.
|  | Carried to summary Euros. |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/2
A | Existing services
Prior to the commencement of any Work, the Contractor is to ascertain from the relevant Authorities the exact position, depth and levels of all existing electric cables, water pipes or other services in the area and he shall make whatever provisions may be required by the Authorities concerned for the support and protection of such services. Any damage or disturbance caused to any service shall be reported immediately to the Project Manager and the relevant Authority and shall be made good to their satisfaction at the Contractors expense.
B | Transport to and from the site
The Contractor shall include in his prices for the transport of materials workmen, etc., to and from the Site of the proposed Works, at such hours and such routes as are permitted by the Authorities
C | Public and private roads, pavements
The Contractor will be required to make good, at his own expense, any damage he may cause to the present road surfaces and pavements during the period of the Works. In particular all the existing lawns, gardens, storm water channels, hedges, fences etc., which may be destroyed or damaged during the progress of the Works are to be made good by the Contractor to the approval of the Project Manager.
D | Security of the works
The Contractor shall be entirely responsible for the security of all the Works, stores, materials, plant, personnel, etc., both of his own and Sub-Contractors’, and shall provide all necessary watching, lighting and other precautions as necessary as to ensure the security and the protection of the public.
E | Water for the works
The Contractor shall allow for providing all temporary water supplies required for the works, including Sub-Contract Works, together with all necessary storage tanks and distribution systems for the same and must allow for bearing all expenses incurred and paying for all water consumed without charge to any Sub-Contractor. Expenses in connection with Nominated Sub-Contractors should be allowed for in the attendance items under the relevant P.C. Sums.
No guarantee or warranty is given as to the availability or suitability of water at the site.
| Carried to summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/3
A | Electric light and power
The Contractor shall allow for providing all temporary lighting and power supplies required for the works, including Sub-Contract works, together with all necessary distribution systems for the same and must allow for bearing all expenses incurred and paying for all current consumed without charge to any Sub-Contractor. Expenses in connection with Nominated Sub-Contractors should be allowed for in the attendance items under the relevant P.C. Sums.
No guarantee or warranty is given as to the availability or suitability of power at the site.
B | Telephone
| The Contractor shall arrange for, provide and maintain a telephone on the Site from the commencement to the completion of the Contract and shall pay all charges in connection therewith. |  |  |  | N/A
C | Temporary Buildings for use by the Contractor
| The Contractor shall at his own cost, supply and erect all temporary buildings, sheds, mess rooms and stores with floors at least 150mm above ground level. No office, stores or other temporary buildings shall be erected on Site without first obtaining the consent from the Project Manager as to the type of temporary building to be supplied and the position in which they are to be erected. |  |  |  | N/A
D | Sheds for storage of Materials
The Contractor shall provide and maintain on the Site, ample weather-proof sheds for storage of cement and other perishable materials and shall clear the same away on completion and make good any disturbed surfaces.
E | Offices for the Consultants
| (i) | The Contractor shall provide, erect and maintain where directed on Site approved weather-proof lockup office for the sole use of the Consultants with a floor area not less than 24 square meters. The office shall be constructed with concrete or wooded floor and the walls and ceiling internally are to be lined with fiberboard. Glazed windows (with curtains or sunshades) shall be provided of not less than 1 meter square area and the door shall have a strong lock or fastening. The office shall be provided with artificial lighting and electric power. The contractor shall allow for regular cleaning of the office. The office is to be furnished with the following : |  |  | N/A
| (a) | 1 No. 20 Seater table, and 20 chairs.
| (b) | 2 No. Pin Boards with a minimum space of 2.0 square metres each
| (c) | 1 No. A0 Size drawing chest with four drawers
| (ii) | The Contractor shall maintain a display of the Programme and Progress chart in the project managers offices, devised in such a way that the lined programme is shown and progress can be marked up as the work proceeds. The Contractor shall keep this chart up to date at all times.
| (iii) | The Contractor shall keep on the Site and maintain in good condition, one dumpy or quickset level and leveling staff and one 30 meters steel/linen tape for the use of the Consultants. The Contractor shall also provide stationery for use by the consultants.
|  | Carried to Summary Euros. |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/4
| (iv) | He shall provide, erect and maintain a lockup pedestal type water closet for the sole use of the Consultants including making temporary connection to drain where applicable to the satisfaction of the Government and Medical officers of Health and shall provide the services of a cleaner and pay all conservancy charges and keep both office and closet clean and in sanitary condition from the commencement to the completion of the Works and dismantle and make good disturbed surfaces to the satisfaction of the Project Manager on completion of the Works.
| (v) | The office and the closet shall be completed before the Contractor is permitted to commence the Works.
A | Office for the Clerk of works / Site Engineer
| The Contractor shall provide, erect and maintain where directed on site an approved weather-proof office for the sole use of the Clerk of Works. The office shall be not less than 12 square meters and shall be of construction similar to the office of the consultants. The office shall as a minimum be furnished with the following: The contractor shall allow for regular cleaning of the office. |  |  |  | N/A
| (a) | 1 No. office desk with lockable drawers, and chair with arm rest, two visitors chairs with armrest
| (b) | 1 No. A0 Size drawing chest with four drawers
| (c) | 1 No. Lockable metal filing cabinet
| (d) | One other office desk and two chairs with armrest
| (e) | 1 No. bookshelf with a minimum of 4 square metres of shelf space
| (f) | 2 No. Pin Boards with a minimum space of 1.5 square metres each
| (g) | Power and Lighting Points as necessary
The contractor shall also supply and maintain the following for the full contract duration, with and including all consumables and maintenance, to the Project Manager's approval:-
| (a) | 1No. fully connected desktop computer with UPS (Dell Optilex GX9020 desktop computers ,Intel Core i7 (3.6GHz,), 16 GB DDR3 RAM,Intergrated 10/100/1000 NIC , 1 ITB HDD 7200rpm , DVD - RW Drive , 18.5" DELL LCD Monitor , DELL keyboard and mouse , Microsoft Windows 10 Pro 64 Bit License accessories as manufactured by Dell or equal approved with one year warranty. This is the minimum to be provided and the Contractor is expected to supply the latest version of both the equipment and software (a laptop of similar specification is also acceptable) |  |  | N/A
| (b) | 1No. Plain paper photocopier, desktop type with variable magnification that can take A3 full size copies, minimum capacity 10copies/minute, including 3kg toner and regular service by agent |  |  | N/A
| (c) | 1No. A3 colour printer
| Carried to Summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/5
| (d) | Full time internet connection |  |  | N/A
| (e) | 1No. 20 mega pixel digital camera with minimum 30-bit colour depth and 2GB memory card as manufactured by Sony or equal approved |  |  | N/A
| (f) | A standard projector and screen. |  |  | N/A
On completion of the project, all equipment will become the property of the Employer.
A | Signboard ( 2 No. each)
The contractor shall provide and erect where directed and maintain during the whole period of building operations and remove at completion, an approved temporary TWO FACED signboard to the Project Manager’s standard design and giving the title of the Works, 3D artistic impression of the project and showing the names of the Employer, Financier, Project Manager, Architect, Quantity Surveyor, Engineers and the Contractor with sufficient space to add the names of the Nominated Sub-Contractors and suppliers. The lettering concerning the Project Manager, Architect, Quantity Surveyor and the Engineer is not to be more than 75mm high.
B | Sanitation of the works
Sanitation of the Works shall be arranged and maintained by the Contractor to the satisfaction of the Government and Local Authorities, Labour Department and the Project Manager.
C | Materials, tools, plant and scaffolding
All materials and workmanship used in the execution of the Works shall be of the best quality and description unless otherwise described. Any materials for the Works condemned by the Project Manager shall immediately be removed from the Site at the Contractor’s expense.
The Contractor shall be responsible for the provision of all materials, scaffolding, tools, plants, transport and workmen required for the Works except insofar as may be stated otherwise herein and he shall allow for the provision of the foregoing except for such items specifically and only required for the use of the Nominated Sub-Contractors as described herein.
No timber used for scaffolding, formwork or similar purpose shall be used afterwards in the permanent Works.
All such plant, tools and scaffolding shall comply with all regulations whether general or local in force throughout the period of the Contract and shall be altered or adapted during the Contract as may be necessary to comply with any amendments in / or additions to such regulations.
D | Supervision and Working hours
The said Works shall be executed under the direction and to the entire satisfaction of the Project Manager ,who shall at all times during normal working hours have access to the Works and to the yards and the workshops of the Contractor and Sub-Contractors or other places where work is being prepared for the Contract.
The working hours shall be those generally worked by good employers in the Building and Civil Engineering Trade in the country. No work shall be carried out at night or on gazetted holidays unless the Project Manager shall so direct.
No work shall be covered up nor shall any concreting be carried out in the absence of the Clerk of Works without the prior approval of the Project Manager in writing.
| Carried to Summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/6
A | Fair wages
| The Contractor shall pay rates of wages and observe hours and conditions of labour not less favourable than the minimum rates of remuneration and minimum conditions of employment applicable in the district in which the works is carried out. The relevant notice must be posted up and kept posted upon the Site where it can conveniently be read by the employees concerned. |  |  |  | N/A
B | Relevant Labour Laws
| The Contractor’s attention is called to the relevant labour laws in the country and the Contractor should allow in the Preliminaries of this Contract for all costs arising or resulting there from. |  |  |  | N/A
C | Labour
| No labour with the exception of the watchman, may be housed on the Site and the Contractor shall allow for all transport and other charges in moving labour to and from the Site at such hours and such routes as are permitted by the Authorities. The Contractor is to provide, erect and maintain satisfactory housing for the watchmen and shall remove the same on completion of the Works. |  |  |  | N/A
D | Existing Property
| The Contractor shall take every precaution to avoid damage to all existing property including roads, cables, drains and other services and he will be held responsible for all damage thereto, arising from the execution of this Contract, and he shall make good all such damages when directed at his own expense. |  |  |  | N/A
E | Protection of the works
The Contractor shall cover up and protect all finished works liable to damage including provision of temporary roofs, gutters, drains, etc., until the completion of the Works.
In the event of any damage occurring to the Works, materials, sewers, drains, gullies, paths or other Works on the Site temporarily in the possession of the Contractor, for the purpose of this Contract, either from the weather, want of proper protection, defects or insufficiency of the Works, the Contractor alone shall be responsible and shall without extra charges, make good all damages and pay all costs which may be levied.
F | Standard Measurements
All dimensions and measures, etc., shown on the Drawings and given in this Bills of Quantities shall be metric.
G | Bills of Quantities
The whole of the Works contained in these Bills of Quantities is measured on the basis of the Standard Method of Measurements of Building and Associated Civil Works for Eastern Africa, prepared by the Architectural Association of Kenya, Quantity Surveyors Chapter, Second Edition, Metric, printed in June 2008.
| Carried to Summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/7
The Method of Measurements herein used must be accepted and will be strictly adhered to for the adjustments of variations or for re-measurements as necessary. The whole of the quantities in these Bills, unless expressly otherwise stated, have been arrived at by taking the net measurements of various items of completed Works from the Drawings.
All the Works in this Contract is liable to re-measurement and no excavation or foundation work or other works shall be filled in or covered up until all re-measurements needed have been made by the Quantity Surveyor.
The rates set out by the Contractor against each item shall, unless otherwise expressly provided to the contrary, or unless there is a separate item for extra labour, cutting or waste, be held to include for waste on materials, carriage and cartage, carrying in and return of empties, hoisting, setting, fitting and fixing in position, making good and all other labours and everything else necessary for the completion of each item and for establishment charges and profit.
Throughout the Bills of Quantities generally, no mention is made of heights for hoisting and all prices must include for hoisting and fixing at any level within the limit shown on the Drawings or included in the general description unless a specific level is stated.
The Contractor shall be deemed to have made allowance in his rates generally to cover items of Preliminaries expenses in connection with P.C Sums or other items if these have not been priced against the respective items.
| Carried to Summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/8
A | Copyright
The copyright of these Bills of Quantities is vested in the Quantity Surveyor and they may not be reproduced in whole or in part without the Quantity Surveyor’s written permission.
B | Prime Cost (P.C.) Sums
| (i) | The words “Prime Cost” (or the initials “P.C”) wherever appearing in these Bills of Quantities, shall mean net cost exclusive of any trade, cash or other discounts whatsoever but inclusive of the cost of packing, carriage and delivery. Such costs shall be the sums due to the Sub-Contractor or suppliers after adjustment where applicable in respect of measurements or rates.
| (ii) | Any increases or decreases in these Prime Cost Sums resulting from the adjustments and properly paid by the Contractor, shall be added to or deducted from the Contract Sum in the final account. In substantiation, the Contractor is required to produce to the Quantity Surveyor, all quotations, invoices and receipted accounts as shall be necessary to show the details of the sums actually paid.
| (iii) | Any sums added by the Contractor in these Bills of Quantities in respect of profit upon any Prime Cost Sums will be deducted in the final settlement of accounts and a sum will be added, the amount of which will bear the same the proportion to the sum added as the net amount properly expended bears to the original P.C.Sum.
C | Samples
The Contractor shall furnish at the earliest possible opportunity before work commences at his own cost, any samples of materials of workmanship that may be called for by the Project Manager for his approval or rejection and any further samples in the case of rejection until such samples are approved by the Project Manager and such samples when approved shall be the minimum standard for the work to which they apply.
D | Proprietary Articles
Where proprietary articles are specified herein, the Contractor may propose the use of materials of equal quality but from other manufacturers with the approval of the Project Manager, but the decision of the Project Manager will be final.
|  | Carried to Summary Euros. |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/9
A | Protection
Cover up and protect from damage, including damage from inclement weather, all finished work and unfixed materials including that of the Sub-Contractor, etc., to the satisfaction of the Project Manager until the completion of the Contract and make good any damage which occurs. Carefully preserve all trees or bushes on or near the site.
B | Removal of plant, Rubbish, etc
The Contractor shall, upon completion of the Works, remove and clear away all temporary buildings, plant, rubbish and unused material, and shall leave the whole of the Site of the Works in a clean and tidy state to the satisfaction of the Project Manager. He shall also remove all rubbish and dirt from the Site at weekly intervals or as directed by the Project Manager.
Particular care shall be taken in leaving windows clean and removal of all paint and cement stains there from.
C | Prevention of Nuisance
The Works and such sections of the Site necessary therefore shall be under the entire care and control of the Contractor during the whole period of the Contract and he shall take all possible precautions to prevent any nuisance, inconvenience or injury to the holders or occupiers of the existing or surrounding properties and to the public generally, and shall at all times keep all the paths and roads affected by the works in a safe and clear state and shall use proper precautions to ensure the safety of all wheeled traffic and pedestrians.
D | Visitors to the site
The Contractor is required to control all visitors to the Site and to keep out unauthorized visitors and to provide a visitors book and ensure that all the authorized visitors sign therein.
|  | Carried to Summary Euros. |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/10
A | Programme and progress
Monthly progress reports shall be prepared by the Contractor and submitted to the Project Manager in six copies. The first report shall cover the period up to the end of the first calendar month following the Commencement Date. Reports shall be submitted monthly thereafter, each within 7 days after the last day of the period to which it relates.
Reporting shall continue until the Contractor has completed all work which is known to be outstanding at the completion date stated in the certificate of practical completion for the Works.
Each report shall include but not limited to:
| (a) | a programme and progress chart devised in such a way that the approved contract work program is shown and progress can be marked up against it as the work proceeds,
| (b) | photographs showing the status of progress on the Site,
| (c) | records of the Contractor's Personnel and Equipment,
| (d) | Site Weather Records dully certified by the Clerk of Works/Site Engineer
| (e) | copies of quality assurance documents, test results and certificates of materials,
| (f) | updated cash flow projection,
| (g) | procurement schedule,
| (h) | safety statistics,
| (i) | comparisons of actual and planned progress, with details of any events or circumstances which may jeopardise the completion in accordance with the Contract, and the measures being (or to be) adopted to overcome the delays.
Following receipt of such a notice, the Contractor shall take such steps as may be necessary, and as the Project Manager may approve, to remedy or mitigate the likely delay, including revision of the programme. The Contractor shall not be entitled to any additional payment for taking such steps.
B | Site progress photographs
The Contractor shall take and develop (in both digital and still form) site progress photographs every two weeks. Adequate copies shall be made for distribution as follows:
| (a) | Client 1 sets in still form & 1 set in digital form.
| (b) | Project Manager 1 set in still form & 1 set in digital form.
| (c) | 1 set of photos in still form to be pinned up in the Site offices for the Consultants.
C | Temporary Hoardings, Fencing and the like
The Contractor shall be entirely responsible for all temporary hoarding and fencing which shall be required by either the Project Manager or the Local Authority. The Contractor should ascertain the extent of such temporary hoardings and fencing and include the costs in his bid.
| Carried to Summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/11
A | Occupational Health and Safety, HIV/AIDS and Gender
The Contract shall provide a qualified safety officer to deal with OHS, HIV/AIDS and Gender Management and provide all necessary facilities including transport. HIV/AIDS and STD prevention and counseling shall include information, education and counseling campaigns including regular distribution of condoms. The Contractor shall provide, maintain and operate a HIV/AIDS and STD clinic or make alternative arrangements with an existing facility to the approval of the Project Manager. The Contractor shall also carry out Gender sensitisation and awareness raising meetings and workshops and provide gender sensitive monitoring and reporting
The Contractor (including his sub-contractors) or any sub-contractor directly employed by the client shall ensure that all health and safety provisions are in place and are functional prior to doing any work on site on a daily basis. Non compliance shall attract an express penalty of EUROS 1,000 (Euros One Thousand only) per day per item listed on the health and safety plan that is not implemented. Such amounts shall be deducted from payment due to main contractor in the valuation that will be issued in the period after the incidence. A letter informing the responsible contractor/sub-contractor of the said undertaking shall be issued by the consultants immediately when the noncompliance is identified.
B | Compliance with NEMA Regulations and the Environment Impact Assessment Report Recommendations
| The Contractor shall comply with all the regulations set out by the National Environmental Management Authority (NEMA). The contractor should familiarize himself with the Recommendations of the Environmental Impact Assessment and comply with them during execution of the work. |  |  |  | N/A
C | As-built drawings and operating & Maintenance Manuals
"As built" drawings and/or operating and maintenance manuals shall be supplied by the Contractor by the date stated in the Conditions of Contract and Contract Data.
D | Occupation Permit
The Contractor shall apply for, provide all transport necessary for, and pay all costs and charges in connection with the Occupation Certificate. Any other supporting documentation required for such certificate will be provided by the Project Manager but the Contractor shall be responsible for producing as-built drawings required for this process in accordance with the Conditions of Contract and the Contract Data.
| Carried to Summary Euros. |  |  |  | 0
| PRELIMINARIES |  |  |  |  | 1/12

## Bill 2.1 NICU REPAIR
PROPOSED REPAIR WORKS OF MCH AT BUGEMBE HCIV
Item | Description | Unit | Qty | Rate (Euro €) | Amount (Euro €)
ELEMENT NO. 1
DEMOLITION
Carefully cut through the wall with angle grinder and create opening for window and doors
A | Window size approx. 1200x1200mm high | No | 1 |  | 0
B | Window size approx. 1400x1500mm high | No | 1 |  | 0
C | Double leaf door size approx. 1200x2400mm high | No. | 1 |  | 0
D | Single leaf door size approx. 900x2400mm high | No. | 1 |  | 0
Carefully remove existing windows and doors and replace with new window & doors (measured seperately) and make good surfaces disturbed
E | Door | No | 1 |  | 0
F | Carefully remove existing oxygen pipe on the wall for reuse | No | 1 |  | 0
G | Carefully remove existing toilet fitting next to nurse station and make good surfaces disturbed | No | 1 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/1/1
ELEMENT NO.2
BRICK WALLING
Ordinary burnt clay brickwork jointed in cement sand (1:3) mortar with and including hoop iron wall ties every alternative course : in
A | 150mm Thick walls externally | SM | 20 |  | 0
B | Allow for repair of minor cracks on the walls and ceilings. | Item | 1 |  | 0
C | Allow for shifting of the oxygen pipes & plumbing system | Item | 1 |  | 0
D | Install timber trap door size 600x600mm | No | 1 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/2/2
ELEMENT NO.3
RAIN WATER DISPOSAL
PVC Key terrain complete with all accessories/fittings; fixed in accordance with manufacturer's instructions
A | 160mm diameter half round PVC gutter complete with gutter clips at 600mm centers | LM | 10 |  | 0
B | Extra over for conner connectors. | NO | 2 |  | 0
C | Extra over gutter for outlet to suit 100mm diameter pipe. | NO | 2 |  | 0
D | Extra over Valley hoppers | NO | 2 |  | 0
E | 100mm diameter PVC down pipe | LM | 20 |  | 0
F | Extra over for bends. | NO | 2 |  | 0
G | Extra over for shoe. | NO | 2 |  | 0
H | Extra over for end connectors. | NO | 2 |  | 0
I | Extra over for gutter straight connectors. | NO | 10 |  | 0
J | Cylindrical PVC vertical water tank 10000 Litres as gentex or equal approved complete with all accessories for rain water harvesting. | NO | 1 |  | 0
K | Platform in grade 20 concrete foundation measurering 2400mm diameter, 600mm high above ground tank base including builders' work. | NO | 1 |  | 0
L | 110mm PN6 PVC pipe from Roof gutters to water tank | LM | 20 |  | 0
M | Soakaway pit size 2000mm wide x 1500deep complete with stone bolders and covered with polythen sheets on top | No | 1 |  | 0
N | Allow for connection accessories and taps | Item | 1 |  | 0
Fire Extinguishers
O | Carbon Dioxide portable fire extinguisher 5kg as NAFFCO CO2 gas extinguisher Model NC5 or equal approved. | NO | 1 |  | 0
P | Dry powder portable fire extinguisher 9 kg as NAFFCO ABC powder Model NP9 or equal approved. | NO | 1 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
2.1/3/3
ELEMENT NO. 4
DOORS
TIMBER DOORS
45mm THICK SOLID CORED FLUSH DOORS; faced both sides with mahogany veneer; with hardwood edge lipping all round: all to Architect's detailed drawings
A | Door D3 Size 1500 x 2400mm high with 5mm think viewing fixed glass panel | NO | 1 |  | 0
B | Door D5 Size 900 x 2100mm high | NO | 1 |  | 0
METAL WORK
PURPOSE MADE DOOR FRAMES AS MANUFACTURED BY ROOFINGS OR EQUAL AND APPROVED: Standard Steel door section complete with fixing accessories and cement sand(1:3) infill; one coat red oxide primer; all to Architect's Drawing
C | 220mm girth rebated to profile x 2mm thick steel frame | LM | 6 |  | 0
D | Ditto to transome | LM | 2 |  | 0
WROT HARDWOOD FRAMES AND LINING selected, treated and kept clean; to Architect's detailed Drawing
E | 70 x 20mm Architrave : two labours | LM | 16 |  | 0
5mm FROSTED SHEET GLASS and glazing as described: to
F | Metal fanlight in panes 0.1 to 0.5 square meters | SM | 2 |  | 0
SUPPLY AND FIX the following ironmongery : locks and furniture where applicable are to be equal to those manufactured by "HAFELE" and approved by the Architect
G | Stainless steel startec single action hinges; Cat No. 926.25.703 | Prs. | 4 |  | 0
H | Stainless steel startec mortise lock; Cat No. 911.24.008 | NO | 2 |  | 0
I | Stainless steel lever handles | Prs. | 2 |  | 0
J | Stainless steel matt escutcheons; Cat No. 903.80.711 | Prs. | 5 |  | 0
K | Star tec stainless steel floor mounted door stop; Cat No. 937.52.070 | NO | 3 |  | 0
L | Push Plates; Cat No. 987.11.300 | NO | 1 |  | 0
M | Startec steven pull handles with straight feet; Cat No. 903.00.705 | NO | 4 |  | 0
N | 800/900 x 300mm high Aluminium Sheet Kick Plate | NO | 4 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
2.1/4/4
ELEMENT NO.5
WINDOWS
CURTAIN RODS
A | 25mm diameter spray painted/galvanised iron hanger rail on and including 100mm diameter x 25mm thick timber end brackets thrice plugged into wall | LM | 17 |  | 0
STEEL CASEMENT WINDOWS
PURPOSE MADE WINDOW STANDARD TO MATCH EXISTING Steel Section for glazing with putty, permanent ventilation comprising T-bar hood and gauze/insect net, standard transomes and mullions, stays and fasteners, one coat red oxide etching primer : including 250mm high vents at the top comprising 3mm thick mild steel sheet cranked louvers, 120mm wide bent to shape all welded to window frame and insect screen; as per Architect's detail drawing
B | Window (W03) Size 1200 x 1200mm high (overall) | NO | 2 |  | 0
PURPOSE MADE STANDARD Steel burglar proofing made from 25 x 4mm flat bar framing and 12mm solid round mild steel bars : one coat red oxide primer as per Architect's detailed drawing
C | Window (W03) Size 1200 x 1200mm high (overall) | NO | 2 |  | 0
D | 6mm thick glass pane to match existing pane on the windows | SM | 4 |  | 0
PREPARE SURFACE AND APPLY ETCHING PRIMER, apply one coat primer, one undercoat and two Gloss finishing coats; on metal work; to
E | Steel windows | SM | 4 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
2.1/5/5
ELEMENT NO.6
INTERNAL FINISHES
WALL FINISHES
INTERNAL LIME PLASTER First coat of cement lime and sand (1:2:9) second coat of cement, lime putty and sand (1:1.6) Steel trowelled smooth
A | 15mm Thick two coat work to walls | SM | 30 |  | 0
POLISHED TERRAZO: FIRST COAT OF 15MM THICK WATERPROOFED CEMENT AND SAND (1:3) SCREED, second coat of 12mm thick coloured cement and approved marble aggregates (1:2;5), including 25 x 3mm pvc dividing strips at 1200mm centres : in
B | 25mm thick to floor | SM | 15 |  | 0
C | 25mm thick clading to Wall | SM | 65 |  | 0
D | Extra over for coved/curved edges of walls | SM | 12 |  | 0
E | 300x150x8mm wall tiling to wall fixed with adhesive joint well grouted and edges line with stainlesss steel or equalapproved materials | SM | 20 |  | 0
Painting and Decorating
PREPARE AND APPLY ONE MIST COAT AND THREE COATS silk vinyl emulsion paint internally on:
F | Plastered surfaces | SM | 170 |  | 0
G | Ceiling surfaces | SM | 80 |  | 0
| PREPARE AND APPLY THREE COATS first grade weatherguard emulsion paint : externally; on |  |  |  | 0
H | Rendered surfaces | SM | 150 |  | 0
I | 300x150x8mm thick ceremic wall tiles fixed with tile adhesive jointwell grouted | SM | 30 |  | 0
J | Ditto floor tiles size 400 X 400X 8mm | SM | 10 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
2.1/6/6
ELEMENT NO.7
MECHANICAL INSTALLATIONS
The Contractor shall supply, deliver,install, test and commission to the satisfaction of the Engineer the following including builders works:-
The Tenderers must allow in their prices for all couplings,connectors as required in the running lengths of pipes.
Sanitary Fittings
Supply and install the following sanitary fittings as specified "OR " Equal and Approved including all necessary fittings and accessories.The contractor shall submit for approval a schedule of fitings before orders for the fittings are placed.
Scrub-up Sink
A | Stainless steel Scrub-up Sink to BS EN 10088/1 1600mm long, wall mounted as 'ARMITAGE SHANKS' S6504 Scrub-up Trough Complete with wall mounted lever action mixer tap as Markwik S8210 or S8215, 1/1/2" plastic resealing bottle trap with removable sump,75mm seal,strainer waste and trap cover. | NO | 0 |  | 0
B | 6mm glass plate mirror size 610x475mm with bevelled edges complete. | NO | 4 |  | 0
0
C | WC Suite - Type 1
| WC Suite, horizontal outlet as Twyfords WC1512WH, , Cover clip CX3648WH, Hinges GR7867WH, Seat ST1304WH, WC Outlet Connector WF1241WH, screwed with approved stainless steel screws, Roll Holder VC9806WH with all connection accesories | No | 1 |  | 0
0
D | Wash Hand Basin - Type 1
| Wash hand Basin as Twyfords Sola WB2522WH, Wall Hangers SR5307XX, Grid waste WF4341CP, Trap WF8463CP, Extension WF8467CP press action pillar tap SF5249CP to approval. | No | 2 |  | 0
Soap Dispenser
E | Stainless steel surface mounted Gel dispenser size 118x115mm, 1.1Litre capacity in a bright finish or approved equivalent. | No | 2 |  | 0
0
Showers
F | Shower mixer complete with all its accessories | No | 2 |  | 0
0
G | Chrome plated Double coat Hooks as Roca or approved equivalent | No | 2 |  | 0
0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/7/7
ELEMENT NO.8
INTERNAL WATER SUPPLY AND DISTRIBUTION
All Cold and Hot Water piping shall be PPR pipe PN25 complete with Tees, Sockets, Elbows, Threaded adapters, Threaded elbows, Reducers and all associated fittings.
PIPE WORK
A | 32mm PPR cold water Pipe work complete. | LM | 30 |  | 0
B | 25mm PPR cold water Pipe work complete. | LM | 30 |  | 0
C | 20mm PPR cold water Pipe work complete. | LM | 30 |  | 0
D | 32mm gate valves | NO | 4 |  | 0
E | 25mm gate valves | NO | 4 |  | 0
F | 20mm angle valves | NO | 4 |  | 0
G | Flexible tube 450mm long complete | NO | 4 |  | 0
H | PVC Gully Trap | NO | 2 |  | 0
I | PVC 4way Floor Trap | NO | 2 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/8/8
FOUL EXTERNAL DRAINAGE SYSTEM- PIPES COMPLETE WITH FITTINGS
The Contractor is to supply ,install and commissionto the satisfaction of the Engineer the followingincluding builders works
A | Excavate trench 0.6M wide ,Max and 1M deep, blind base of trench and cover drianage pipe with sand minimum 50mm thick before back fill excess soil over laid drainage pipes | LM | 30 |  | 0
B | uPVC pipe 32mm PN 6 to be laid as detailed | LM | 20 |  | 0
C | uPVC pipe 50mm PN 6 to be laid as detailed | LM | 30 |  | 0
D | uPVC pipe 110mm PN 6 to be laid as detailed | LM | 30 |  | 0
E | uPVC pipe 150mm PN 6 to be laid as detailed | LM | 5 |  | 0
F | Manhole as 600 x 450mm (internally) inspection chambers 600mm deep invert consisting of 150mm thick concrete block wall, benched and channeled in concrete Class "Q' and rendered and trowelled smooth in 20mm thick water proofed cement/sand screed including excavation and medium duty approved cast iron cover and frame | NO | 2 |  | 0
G | Ditto Gully traps 300x300mm with medium duty approved cast iron cover and frame | NO | 2 |  | 0
H | Soakpit size 3M diam 2M deep filled with hard core and covered with 1000 guage polythene and top made good to match surroundings | NO | 1 |  | 0
0
I | Ditto but size2M diam 1.5M deep | NO | 1 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/8/9
ELEMENT NO.9
ELECTRICAL INSTALLATIONS
Socket points
A | Double sockets wired by 2.5mm2 copper cables in 25mm heavy guage PVC surface conduit complete with MK boxes and all accessories. | NO | 6 |  | 0
B | Supply and install 2.5mm² PVC-Insulated twin and earth copper cables drawn in 25mm heavy guage PVC surface conduit | LM | 25 |  | 0
C | 25mm PVC heavy gauge conduit to allow for concealed wiring | LM | 25 |  | 0
Earthing and Lightning Protection
A | Air terminal 16mm diameter, 1200mm long, complete with tape adapters, spikes and all accessories by FURSE or HEX or equal approved. | No | 1 |  | 0
B | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or HEX or equal. | Lm | 20 |  | 0
C | Test clamp complete as by FURSE or HEX or equal. | No | 1 |  | 0
D | Supply and install 600mmx600mm earthing mat at a depth of at least 0.5m | No | 1 |  | 0
E | General Earthing by 16mm2 stranded bare copper cable complete with all accessories. | Lm | 20 |  | 0
F | Precast Inspection chamber of 300mmx300mm complete with cover made of grade 25 concrete | m3 | 0.05 |  | 0
G | Earthing: excavate pit 1500x1200x1500mm (LxWxD) and place course salt mixed with charcoal dust and soil in pit and compact and drive electrodes into this pit, connect and place precast manhole and connect up ready and measure the resistance. | No | 1 |  | 0
H | Allow for 32mm heavy duty gauge PVC conduit for concealing the copper tape | LM | 5 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
ELEMENT NO.10
Operation and maintenance manual
Visual information & knowledge management
The following items will be supplied and/installed for the purpose of Maintenance and Operations of the installed systems
A | Operational manual; Comprehensive Operation and Maintenance manual for the structures renovated, newly build and installed system, written in English and graphically illustrated for unambiguous interpretation and understanding by Operation and Maintenance staff. Special attention shall be drawn to fault finding and remedial action. The manual shall include a system wiring diagram , a list of spare parts and the names of the accredited suppliers/agents of these spare parts. The manual shall also include the manufacturer's name, model number, service manuals, parts list and brief descriptions of all equipment and their basic operating features i.e. routine maintenance procedures, possible breakdowns and repairs, recommended spare parts, troubleshooting guide, equipment layout and simplified wiring and control diagrams of the system as installed. | pcs | 1 |  | 0
B | Component signage; each component of the installed structure/systems should be clearly labelled onto sticker paper or equal/better approved material and securely mounted directly adjacent to the component. The lettering shall be high contrast and no less than 50mm and no more than 75mm in size. Sites where only specific components are being replaced will be treated similarly to sites where full installations will be done; i.e. labels will also be installed against all existing components of systems where the contractor only replaces certain parts. | Ls | 1 |  | 0
C | As built drawing for the buildings and system chart (electrical & mechanical layout, ); an A1 size chart showing the entire system with its parts and wiring/plumbing, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 |  | 0
D | Error/warning chart; an A1 size chart illustrating common warning signs and error messages, and their meanings, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/9/10
COLLECTION
0
0
0
0
0
0
0
0
0
0
0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
3.1/9/11

## Bill 3.1 KITCHEN CONSTRUCTION
PROPOSED CONSTRUCTION OF PATIENCE KITCHEN AT BUGEMBE HCIV JINJA DISTRICT
Item | Description | Unit | Qty | Rate (Euro €) | Amount (Euro €)
ELEMENT NO. 1
SUBSTRUCTURES
ALL PROVISIONAL
The work in this element includes all works up to and including the ground floor slab
A | Allow for maintaining and upholding sides of excavation: clear off all fallen material, rubbish | ITEM | 1 |  | 0
B | Allow for keeping the whole of the excavation free from general water | ITEM | 1 |  | 0
C | Excavate oversite to remove vegetable top soil; remove from site | SM | 150 |  | 0
D | Mass excavation to reduce levels average 200mm deep commencing from stripped level; remove from site. | CM | 30 |  | 0
E | Excavate for foundation trench not exceeding 1.5 meters deep from reduced level. | CM | 24 |  | 0
F | Excavate for column pad not exceeding 1.5 meters deep from reduced level. | CM | 6 |  | 0
G | Extra over excavations for excavating in rock. | CM | 10 |  | 0
H | Return fill and ram selected excavated material around foundations. | CM | 30 |  | 0
I | Load and cart away surplus excavated material from site. | CM | 10 |  | 0
J | Approved imported marrum fill to make up levels; well rolled and compacted in layers not exceeding 150mm thick to 98% MDD to Engineer's approval | CM | 30 |  | 0
K | 200mm Thick bed of hand packed stone base, well rolled and compacted. | SM | 35 |  | 0
L | 50mm thick stone dust blinding over surfaces of hardcore | SM | 35 |  | 0
M | Anti-termite treatment as Termidor or other equal and approved to surfaces of hardcore, top of foundation walling and bottom of excavation. | SM | 35 |  | 0
CONCRETE WORK
PLAIN CONCRETE CLASS 15; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE)
N | 100mm Thick blinding layer under strip foundations | SM | 20 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/1/1
ELEMENT NO. 1
VIBRATED REINFORCED CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:
A | Strip foundations | CM | 6 |  | 0
B | 120mm thick ground floor slab | SM | 35 |  | 0
C | Stub coloumn | CM | 1 |  | 0
STEEL FABRIC REINFORCEMENT TO BS 4483 as described
D | No. A142 Fabric Mesh reinforcement weighing 2.22 kg. per square meter fixed in slab | SM | 35 |  | 0
FORMWORK TO
E | Sides of column stub | SM | 8 |  | 0
F | Edges of slabs 75 to 150mm high | LM | 25 |  | 0
| DAMP PROOF COURSES |  |  |  | 0
G | 1000 Gauge polythene sheeting laid on blinded hardcore | SM | 35 |  | 0
WALLING
Solid concrete blockwork jointed and pointed in cement sand (1:3) mortar : with and including hoop iron wall ties every alternative course : in
H | 200mm Thick walls | SM | 55 |  | 0
SUNDRIES
I | 20 SWG Hoop Iron wall tie 25mm wide x 450mm long cast 75mm into concrete and built into joint of block walling | NO | 14 |  | 0
TWO COATS EXTERNAL CEMENT RENDER (1:4) finished with wood float
J | 15mm thick to walls | SM | 55 |  | 0
TWO COATS BLACK BITUMASTIC paint : on
K | Rendered walls | SM | 55 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/1/2
ELEMENT NO.1
STEEL REINFORCEMENT as described including cutting to length, bending, hoisting and fixing and including all necessary tying wire and spacing blocks
HIGH YIELD RIBBED BARS, TYPE 2 TO BS 4449:2005
A | 8mm Diameter bars | KG | 30 |  | 0
B | 12mm Diameter bars | KG | 60 |  | 0
FORMWORK TO:
C | Sides of stub column | SM | 8 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/1/3
ELEMENT NO. 2
R.C. FRAME
CONCRETE WORK
VIBRATED REINFORCED CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:
A | Column & Ring beams | CM | 3 |  | 0
STEEL REINFORCEMENT as described including cutting to length, bending, hoisting and fixing and including all necessary tying wire and spacing blocks
HIGH YIELD RIBBED BARS, TYPE 2 TO BS 4449:2005
B | 8mm Diameter bars | KG | 100 |  | 0
C | 12mm Diameter bars | KG | 170 |  | 0
FORMWORK TO:
D | Sides and soffittes of column and ring beams | SM | 35 |  | 0
BRICK WALLING
Solid concrete blockwork jointed and pointed in cement sand (1:3) mortar : with and including hoop iron wall ties every alternative course : in
E | 200mm Thick walls externally | SM | 70 |  | 0
F | 150mm Thick walls externally | SM | 30 |  | 0
Supply, install, connect and set to work the following:
Energy Saving Wood Stoves
G | Allow a provisional sum of 6,000 euro for construction of 12No. 5 litres capacity energy saving wood stove complete with the following in accordance with the drawings: i) In-built cooking chamber of heat resistant (refractory) brick wall externally finished in facing bricks, ii) firewood magazine combustion chamber, (iii) air inlet and (iv) chimney with cap at base for soot removal. | Item | 1 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/2/4
ELEMENT NO. 3
Structural Steelwork
THE RATES FOR STRUCTURAL STEEL WORK SHOULD INCLUDE ALL PLATES, STIFFENERS, BOLTS, WELDED JOINTS, ALL CONNECTIONS AND ACCESSORIES; PAINTING AND DECORATIONS; AS PER THE ARCHITECT’S AND STRUCTURAL ENGINEERS DRAWINGS; THE CONTRACTOR MUST STUDY THE DRAWINGS AND ENSURE THAT HIS PRICE INCLUDES ALL ITEMS AS SHOWN ON THE DRAWINGS
Structural Steelwork : framed : one coat red-oxide primer;
A | 70 x 70 x 3mm RHS rafters | KG | 400 |  | 0
B | 70 x 70 x 3mm RHS tie beam | KG | 250 |  | 0
C | 70 x 70 x 3mm RHS struts and tie | KG | 500 |  | 0
D | Z purlin 150x50x2mm | Kg | 300 |  | 0
E | Facia boards 200x30x1.5mm | Kg | 170 |  | 0
Supply and fix the following in fabricated mild steel sections including special purpose made j-bolts other specified connections and fastenings; one coat of specified primer before erection ; 3-coats gloss paint after erection all above measured inclusive
F | 26 Gauge pre-painted IT4 roofing sheets : fixed to GI- purlins with self tapping screws : in Sheet laid sloping not exceeding 15 degrees from horizontal. | SM | 80 |  | 0
G | Prepare and apply one coat undercoat and two finishing coats oil emulsion paint to all steel section | kg | 1620 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
2.1/3/5
ELEMENT NO.4
WORKTOP SIZE 2800x350x900MM HIGH & 2800x600x900MM HIGH
BRICK WORK
Ordinary burnt clay brickwork jointed in cement sand (1:3) mortar with and including hoop iron wall ties every alternative course : in
A | 150mm thick walls | SM | 12 |  | 0
CONCRETE WORK
VIBRATED REINFORCED CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:
B | 75mm thick concrete slab | SM | 10 |  | 0
STEEL REINFORCEMENT as described including cutting to length, bending, hoisting and fixing and including all necessary tying wire and spacing blocks
HIGH YIELD RIBBED BARS, TYPE 2 TO BS 4449:2005
C | 10mm Diameter bars | KG | 35 |  | 0
FORMWORK TO:
D | 75mm wide to sides of slab | LM | 20 |  | 0
E | Sofit of slab | SM | 10 |  | 0
FINISHES
Wall plater cement sand mix 1:4 steel trowelled smooth
F | 15mm thick to walls | SM | 10 |  | 0
G | 20mm thick granite worktop finish | SM | 10 |  | 0
H | 20mm thick granite wall finish | SM | 24 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/4/6
ELEMENT NO.5
WASH FACILITY
BRICK WORK
Ordinary burnt clay brickwork jointed in cement sand (1:3) mortar with and including hoop iron wall ties every alternative course : in
A | 150mm thick walls | SM | 3 |  | 0
B | 230mm thick walls | SM | 3 |  | 0
CONCRETE WORK
VIBRATED REINFORCED CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:
C | 75mm thick concrete slab | SM | 7 |  | 0
STEEL REINFORCEMENT as described including cutting to length, bending, hoisting and fixing and including all necessary tying wire and spacing blocks
HIGH YIELD RIBBED BARS, TYPE 2 TO BS 4449:2005
D | 10mm Diameter bars | KG | 30 |  | 0
FORMWORK TO:
E | 75mm wide to sides of slab | LM | 10 |  | 0
F | Sofit of slab | SM | 7 |  | 0
FINISHES
Wall plater cement sand mix 1:4 steel trowelled smooth
G | 15mm thick to walls | SM | 15 |  | 0
0
H | 20mm thick granite worktop finish | SM | 7 |  | 0
I | 20mm thick granite wall finish | SM | 8 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/5/7
ELEMENT NO.6
RAIN WATER DISPOSAL
PVC Key terrain complete with all accessories/fittings; fixed in accordance with manufacturer's instructions
A | 160mm diameter half round PVC gutter complete with gutter clips at 600mm centers | LM | 20 |  | 0
B | Extra over gutter for outlet to suit 100mm diameter pipe. | NO | 2 |  | 0
C | 100mm diameter PVC down pipe | LM | 12 |  | 0
D | Extra over for bends. | NO | 6 |  | 0
E | Extra over for shoe. | NO | 4 |  | 0
F | Extra over for end connectors. | NO | 4 |  | 0
G | Extra over for gutter straight connectors. | NO | 2 |  | 0
Fire Extinguishers
H | Carbon Dioxide portable fire extinguisher 5kg as NAFFCO CO2 gas extinguisher Model NC5 or equal approved. | NO | 1 |  | 0
I | Dry powder portable fire extinguisher 9 kg as NAFFCO ABC powder Model NP9 or equal approved. | NO | 1 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
3.1/6/8
ELEMENT NO.7
SPLASH APRON
EXCAVATIONS
A | Excavate for strip foundationhh commencing at reduced level but not exceeding 1.5m deep; deposit in temporary spoil heaps on site. | CM | 8 |  | 0
B | Load and cart away surplus excavated material away from site. | CM | 3 |  | 0
C | Return, fill in and ram selected excavated materials around foundation. | CM | 5 |  | 0
D | Approved marram fill to make up levels; well rolled and compacted to 95% MDD in layers not exceeding 150mm thick. Overall 400mm thick | CM | 5 |  | 0
E | 150mm Thick bed of hand packed stone base, well rolled and compacted | SM | 15 |  | 0
F | 50mm Thick sand blinding over surfaces of hard core. | SM | 15 |  | 0
CONCRETE WORK
PLAIN CONCRETE CLASS 15 (20mm AGGREGATE)
G | 50mm Thick blinding layer under strip foundation. | SM | 15 |  | 0
BRICK WORK well, burnt clay bricks built in cement sand (1:3) mortar and including hoop iron ties every alternate course: in 150mm Thick walls
Brick work jointed and pointed in cement sand (1:3) mortar with and including hoop iron ties every alternate course : in
H | 150mm Thick walls | SM | 25 |  | 0
| FINISHES |  | -
CEMENT SAND (1:4) Render finished smooth
I | 15mm thick to walls finished smooth | SM | 25 |  | 0
PAINTING
J | Prepare and apply three coats of bituminous paint to rendered surfaces | SM | 25 |  | 0
K | VIBRATED MASS CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:75mm thick slab on the apron and well finished using power floating. | SM | 20 |  | 0
Aspron finishes
L | Cement sand screed mix 1:3 floor finish | SM | 15 |  | 0
M | 15mm thick Cement sand mix 1:3plaster to walls | SM | 18 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
3.1/7/9
ELEMENT NO.8
INTERNAL & EXTERNAL FINISHES
WALL FINISHES
INTERNAL LIME PLASTER First coat of cement lime and sand (1:2:9) second coat of cement, lime putty and sand (1:1.6) Steel trowelled smooth
A | 15mm Thick two coat work to walls | SM | 150 |  | 0
EXTERNAL CEMENT SAND PLASTER cementand sand (1:3) Steel trowelled smooth
B | 20mm Thick two coat work to walls | SM | 90 |  | 0
PAINTING AND DECORATING
PREPARE AND APPLY ONE MIST COAT AND THREE COATS silk vinyl emulsion paint internally on:
C | Plastered surfaces | SM | 150 |  | 0
PREPARE AND APPLY THREE COATS first grade weatherguard emulsion paint : externally; on
D | Rendered surfaces | SM | 90 |  | 0
FLOOR FINISHES
POLISHED TERRAZO: FIRST COAT OF 15MM THICK WATERPROOFED CEMENT AND SAND (1:3) SCREED, second coat of 12mm thick coloured cement and approved marble aggregates (1:2;5), including 25 x 3mm pvc dividing strips at 1200mm centres : in
E | 25mm thick to floor | SM | 35 |  | 0
F | 25mm thick clading to Wall | LM | 40 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
3.1/8/10
ELEMENT NO.9
MECHANICAL INSTALLATIONS
The Contractor shall supply, deliver,install, test and commission to the satisfaction of the Engineer the following including builders works:-
The Tenderers must allow in their prices for all couplings,connectors as required in the running lengths of pipes.
Sanitary Fittings
Supply and install the following sanitary fittings as specified "OR " Equal and Approved including all necessary fittings and accessories.The contractor shall submit for approval a schedule of fitings before orders for the fittings are placed.
Kitchen sink
A | Stainless steel Sink single drain, Complete with wall mounted lever action mixer tap as Markwik S8210 or S8215, 1/1/2" plastic resealing bottle trap with removable sump,75mm seal,strainer waste and trap cover. | NO | 4 |  | 0
0
| FOUL EXTERNAL DRAINAGE SYSTEM- PIPES COMPLETE WITH FITTINGS |  |  |  | 0
| The Contractor is to supply ,install and commissionto the satisfaction of the Engineer the followingincluding builders works |  |  |  | 0
B | Excavate trench 0.6M wide ,Max and 1M deep, blind base of trench and cover drianage pipe with sand minimum 50mm thick before back fill excess soil over laid drainage pipes | LM | 30 |  | 0
C | uPVC pipe 32mm PN 6 to be laid as detailed | LM | 15 |  | 0
D | uPVC pipe 50mm PN 6 to be laid as detailed | LM | 15 |  | 0
E | uPVC pipe 110mm PN 6 to be laid as detailed | LM | 10 |  | 0
F | uPVC pipe 150mm PN 6 to be laid as detailed | LM | 20 |  | 0
G | Manhole as 600 x 450mm (internally) inspection chambers 600mm deep invert consisting of 150mm thick concrete block wall, benched and channeled in concrete Class "Q' and rendered and trowelled smooth in 20mm thick water proofed cement/sand screed including excavation and medium duty approved cast iron cover and frame | NO | 2 |  | 0
H | Ditto Gully traps 300x300mm with medium duty approved cast iron cover and frame | NO | 2 |  | 0
I | Soakpit size 2M diam 1.5M deep filled with hard core and covered with 1000 guage polythene and top made good to match surroundings | NO | 2 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/9/11
ELEMENT NO.10
INTERNAL WATER SUPPLY AND DISTRIBUTION
All Cold and Hot Water piping shall be PPR pipe PN25 complete with Tees, Sockets, Elbows, Threaded adapters, Threaded elbows, Reducers and all associated fittings.
PIPE WORK
A | 32mm PPR cold water Pipe work complete. | LM | 20 |  | 0
B | 25mm PPR cold water Pipe work complete. | LM | 20 |  | 0
C | 20mm PPR cold water Pipe work complete. | LM | 20 |  | 0
D | 32mm gate valves | NO | 4 |  | 0
E | 25mm gate valves | NO | 4 |  | 0
F | 20mm angle valves | NO | 4 |  | 0
G | Flexible tube 450mm long complete | NO | 4 |  | 0
H | PVC Gully Trap | NO | 4 |  | 0
I | PVC 4way Floor Trap | NO | 4 |  | 0
Wiring and lighting
J | Lighting points wired by 1.5mm2 copper cables in 25mm heavy guage PVC wall concealed conduit complete with MK boxes,1W1G switches and all accessories. | NO | 2 |  | 0
K | Water proof LED luminaire with replaceable LED Tubes, 4ft, IP65, IK08, 20W complete with all accessories | NO | 2 |  | 0
L | Supply and install weatherproof LED floodlight, minimum power rating 20W, IP65-rated for outdoor use, complete with all necessary accessories including mounting bracket, fixing screws, internal driver, switches and wiring for connection to 220–240V AC supply. | NO | 2 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
3.1/10/12
COLLECTION
| Total carried forward from Page 3.1/1/1 |  |  |  | 0
| Total carried forward from Page 3.1/1/2 |  |  |  | 0
| Total carried forward from Page 3.1/1/3 |  |  |  | 0
| Total carried forward from Page 3.1/2/4 |  |  |  | 0
| Total carried forward from Page 3.1/3/5 |  |  |  | 0
| Total carried forward from Page 3.1/4/6 |  |  |  | 0
| Total carried forward from Page 3.1/5/7 |  |  |  | 0
| Total carried forward from Page 3.1/6/8 |  |  |  | 0
| Total carried forward from Page 3.1/7/9 |  |  |  | 0
| Total carried forward from Page 3.1/8/10 |  |  |  | 0
| Total carried forward from Page 3.1/9/11 |  |  |  | 0
| Total carried forward from Page 3.1/10/12 |  |  |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
3.1/11/12

## Bill 4.1 Walkway construction
PROPOSED CONSTRUCTION OF COVERED WALKWAY AT BWUGEMBE HEALTH CENTRE IV, JINJA DISTRICT.
ITEM | DESCRIPTION | UNIT | QTY | RATE (EURO) | AMOUNT EURO)
ELEMENT NO 1: WALKWAY CONSTRUCTION
Site Preparation
A | Excavate top vegetable soil average 150mm deep and cart to spoil | SM | 100 |  | 0
B | Anti-termite treatment to stripped surfaces of ground | SM | 100 |  | 0
Disposal of excavated materials
C | Surplus excavated material: Load up, cart, deposit, spread and level on site where directed. | CM | 8 |  | 0
Fillings
D | Approved Gravel soil filling : well watered and compacted to MOD 95%: to make up levels under floor bed | CM | 12 |  | 0
Walkway floor
E | 450x 450x75mm thick precast concrete reinofrced slabs, slabs reinforced with10mm bar spaced at 150mm centers both ways, laid on compacted imported murram, on 50mm thick sand bedding including filling joint swith cement and sand mortar 1:3 | SM | 50 |  | 0
Hardcore filling
F | 200mm Thick hardcore filling well compacted to making up levels | SM | 50 |  | 0
CONCRETE WORK
VIBRATED REINFORCED CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:
G | Base of stachion | CM | 3 |  | 0
H | 100mm strip foundation | SM | 16 |  | 0
Kerb stones
I | 125mm x 300mmx 900mm Half-battered kerbs to BS 340 bedded and jointed in cement sand (1:3) mortar on and including 450mm x 200mm thick concrete grade 20 bed and 100mm hauching at back including all necessary excavation and formwork | LM | 55 |  | 0
Prepare and apply one coat undercoat and two finishing coats road marking paint to:
J | Half battered kerb stones. | LM | 55 |  | 0
| Total carried to collection |  |  |  | 0
4.1/1/1
ITEM | DESCRIPTION | UNIT | QTY |  | AMOUNT (UGX)
ELEMENT NO 2: WALKWAY CONSTRUCTION CON'TD
Stanchion - poles
A | 75mm diameter x 3mm thick Round Hollow Section stanchion: Height 2800mm long including 400-700mm length bedded in concrete in ground : top welded with 2mm thick U-shaped mild steel cleat to receive wall plate (m/s):bottom welded with fixing lugs: primed with one coat red oxide primer before fixing. | Kg | 450 |  | 0
VIBRATED REINFORCED CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:
B | Foundation pits to receive steel poles | CM | 3 |  | 0
C | Form work to sides of concrete | SM | 25 |  | 0
Roof covering
Supply and fix the following in fabricated mild steel sections including special purpose made j-bolts other specified connections and fastenings; one coat of specified primer before erection ; 3-coats gloss paint after erection all above measured inclusive
D | 26 Gauge pre-painted IT4 roofing sheets : fixed to GI- purlins with self tapping screws : in Sheet laid sloping not exceeding 15 degrees from horizontal. | SM | 80 |  | 0
Roof structure
E | 50x50x2mm thick Hollow Section Rafter: length to GI Poles with anchors. | Kg | 300 |  | 0
F | Round hollow section 75x3mm steel post | Kg | 450 |  | 0
G | Wall plate 50x50x2mm | Kg | 650 |  | 0
H | Guard rails 25x25x2mm | Kg | 700 |  | 0
I | Z purlin 150x50x2mm | Kg | 640 |  | 0
J | Facia boards 200x30x1.5mm | Kg | 560 |  | 0
K | M.S base plate 6mm thick complete with 4no. 17mm diameter hole on each plate | Kg | 200 |  | 0
L | 16mmdiameter bolts | No | 120 |  | 0
M | 8mm diameter bolts | No | 120 |  | 0
N | Prepare and apply one coat undercoat and two finishing coats oil emulsion paint to all steel section | kg | 3250 |  | 0
| Total carried to collection |  |  |  | 0
ELEMENT NO 3: WALKWAY CONSTRUCTION CON'TD
Wiring and lighting
A | Lighting switches 2W2G wired by 2.5mm2 copper cables in 25mm heavy guage PVC surface conduit complete with MK boxes and all accessories. | NO | 2 |  | 0
B | Supply and install 2.5mm² PVC-Insulated twin copper cables drawn in 25mm heavy guage PVC surface conduit | LM | 40 |  | 0
C | 25mm PVC heavy gauge conduit to allow for concealed wiring | LM | 40 |  | 0
D | Adaptable box with TPN 32A connector block. | NO | 1 |  | 0
E | Water proof LED luminaire with replaceable LED Tubes, 4ft, IP65, IK08, 20W complete with all accessories | NO | 4 |  | 0
F | Allow for supply of all the necessary accessories such as MK boxes, junction boxes, insulting tape, tower clips, nails, strip connectors, wall plugs, self taping screws, etc. | ITEM | 1 |  | 0
| Total carried to collection |  |  |  | 0
COLLECTION
| Total carried forward from Page 4.1/1/1 |  |  |  | 0
| Total carried forward from Page 4.1/2/2 |  |  |  | 0
| Total carried forward from Page 4.1/3/3 |  |  |  | 0
| Total to Summary |  |  |  | 0
4.1/3/3

## Bill 5.1 EXTERNAL TOILET
PROPOSED RENOVATION OF TOILET AT BUGEMBE HCIV JINJA DISTRICT
Item | Description | Unit | Qty | Rate (Euro €) | Amount (Euro €)
ELEMENT NO. 1
DEMOLITION
Carefully cut through the wall with with and angle grinder and create opening for window and doors
A | Single leaf door size approx. 900x2400mm high | No. | 2 |  | 0
B | Carefully remove existing toilet pan and appropriately disposed off. | No | 2 |  | 0
C | Hack off section of existing wall plaster | SM | 20 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
5.1/1/1
ELEMENT NO.2
STEEL DOORS
Purpose made steel casement doors manufactured from standard W20 sections: manufacture, assemble and deliver to site : Supply and fix ironmongery comprising approved hinges, pivoting mechanisms, stays, fasteners to opening lights: plugged and screwed or built into walling : one coat red oxide primer before delivery.
| Door size 900 x 2400mm high | NO | 2 |  | 0
PREPARE SURFACE AND APPLY ETCHING PRIMER, apply one coat primer, one undercoat and two Gloss finishing coats; on metal work; to
| Steel door complete with burglar proofing | SM | 13 |  | 0
SUPPLY AND FIX the following ironmongery : locks and furniture where applicable are to be equal to those manufactured by "HAFELE" and approved by the Architect
G | Stainless steel startec single action hinges; Cat No. 926.25.703 | Prs. | 3 |  | 0
J | Stainless steel startec mortise lock; Cat No. 911.24.008 | NO | 2 |  | 0
K | Stainless steel lever handles | Prs. | 2 |  | 0
M | Star tec stainless steel floor mounted door stop; Cat No. 937.52.070 | NO | 2 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
5.1/2/2
ELEMENT NO.3
SPLASH APRON
EXCAVATIONS
A | Excavate for around existing foundation to reduced level below that of the apron; deposit in temporary spoil heaps on site. | CM | 4 |  | 0
B | Load and cart away surplus excavated material away from site. | CM | 2 |  | 0
C | Return, fill in and ram selected excavated materials around foundation. | CM | 2 |  | 0
D | Approved marram fill to make up levels; well rolled and compacted to 95% MDD in layers not exceeding 150mm thick. Overall 400mm thick | CM | 3 |  | 0
BRICK WORK well, burnt clay bricks built in cement sand (1:3) mortar and including hoop iron ties every alternate course: in 150mm Thick walls
Brick work jointed and pointed in cement sand (1:3) mortar with and including hoop iron ties every alternate course : in
E | 150mm Thick walls | SM | 10 |  | 0
| FINISHES |  | -
CEMENT SAND (1:4) Render finished smooth
F | 15mm thick to walls finished smooth | SM | 10 |  | 0
PAINTING
G | Prepare and apply three coats of bituminous paint to rendered surfaces | SM | 10 |  | 0
H | VIBRATED MASS CONCRETE CLASS 25; ORDINARY PORTLAND CEMENT 42.5 (20MM AGGREGATE) IN:75mm thick slab on the apron and well finished using power floating. | SM | 15 |  | 0
Aspron finishes
I | Cement sand screed mix 1:3 floor finish | SM | 15 |  | 0
J | 15mm thick Cement sand mix 1:3plaster to walls | SM | 10 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
5.1/3/3
ELEMENT NO.4
INTERNAL & EXTERNAL FINISHES
WALL FINISHES
INTERNAL LIME PLASTER First coat of cement lime and sand (1:2:9) second coat of cement, lime putty and sand (1:1.6) Steel trowelled smooth
A | 15mm Thick two coat work to walls | SM | 20 |  | 0
EXTERNAL CEMENT SAND PLASTER cementand sand (1:3) Steel trowelled smooth
B | 20mm Thick two coat work to walls | SM | 10 |  | 0
PAINTING AND DECORATING
PREPARE AND APPLY ONE MIST COAT AND THREE COATS silk vinyl emulsion paint internally on:
C | Plastered surfaces | SM | 40 |  | 0
D | ceiling surfaces | SM | 10 |  | 0
PREPARE AND APPLY THREE COATS first grade weatherguard emulsion paint : externally; on
E | Rendered surfaces | SM | 30 |  | 0
FLOOR FINISHES
POLISHED TERRAZO: FIRST COAT OF 15MM THICK WATERPROOFED CEMENT AND SAND (1:3) SCREED, second coat of 12mm thick coloured cement and approved marble aggregates (1:2;5), including 25 x 3mm pvc dividing strips at 1200mm centres : in
F | 25mm thick to floor | SM | 10 |  | 0
G | 25mm thick clading to Wall | LM | 25 |  | 0
H | 300x150x8mm thick ceremic wall tiles fixed with tile adhesive jointwell grouted | SM | 30 |  | 0
3mm thick (each) EPDM APP modified bituminous water proofing membrane, reinforced with polyester, fully bonded and torch applied onto solvent base primer conforming to ASTMD- 41 applied in accordance with manufacturers instructions; to
I | Well prepare flat roofs surface | SM | 10 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
5.1/4/4
ELEMENT NO.5
MECHANICAL INSTALLATIONS
The Contractor shall supply, deliver,install, test and commission to the satisfaction of the Engineer the following including builders works:-
The Tenderers must allow in their prices for all couplings,connectors as required in the running lengths of pipes.
Sanitary Fittings
Supply and install the following sanitary fittings as specified "OR " Equal and Approved including all necessary fittings and accessories.The contractor shall submit for approval a schedule of fitings before orders for the fittings are placed.
Toilet system
A | Low level sitting pan type toilet system | NO | 1 |  | 0
B | Shower system complete with the mixer | NO | 1 |  | 0
0
0
| FOUL EXTERNAL DRAINAGE SYSTEM- PIPES COMPLETE WITH FITTINGS |  |  |  | 0
| The Contractor is to supply ,install and commissionto the satisfaction of the Engineer the followingincluding builders works |  |  |  | 0
C | Excavate trench 0.6M wide ,Max and 1M deep, blind base of trench and cover drianage pipe with sand minimum 50mm thick before back fill excess soil over laid drainage pipes | LM | 10 |  | 0
D | uPVC pipe 32mm PN 6 to be laid as detailed | LM | 15 |  | 0
E | uPVC pipe 50mm PN 6 to be laid as detailed | LM | 5 |  | 0
F | uPVC pipe 110mm PN 6 to be laid as detailed | LM | 5 |  | 0
G | uPVC pipe 150mm PN 6 to be laid as detailed | LM | 10 |  | 0
H | Manhole as 600 x 450mm (internally) inspection chambers 600mm deep invert consisting of 150mm thick concrete block wall, benched and channeled in concrete Class "Q' and rendered and trowelled smooth in 20mm thick water proofed cement/sand screed including excavation and medium duty approved cast iron cover and frame | NO | 1 |  | 0
I | Ditto Gully traps 300x300mm with medium duty approved cast iron cover and frame | NO | 1 |  | 0
J | Soakpit size 2M diam 1.5M deep filled with hard core and covered with 1000 guage polythene and top made good to match surroundings | NO | 1 |  | 0
0
K | Cylindrical PVC vertical water tank 3000 Litres as gentex or equal approved complete with all accessories for rain water harvesting. | NO | 1 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
5.1/5/5
ELEMENT NO.6
INTERNAL WATER SUPPLY AND DISTRIBUTION
All Cold and Hot Water piping shall be PPR pipe PN25 complete with Tees, Sockets, Elbows, Threaded adapters, Threaded elbows, Reducers and all associated fittings.
PIPE WORK
A | 32mm PPR cold water Pipe work complete. | LM | 20 |  | 0
B | 25mm PPR cold water Pipe work complete. | LM | 15 |  | 0
C | 20mm PPR cold water Pipe work complete. | LM | 15 |  | 0
D | 32mm gate valves | NO | 1 |  | 0
E | 25mm gate valves | NO | 1 |  | 0
F | 20mm angle valves | NO | 2 |  | 0
G | Flexible tube 450mm long complete | NO | 2 |  | 0
H | PVC Gully Trap | NO | 1 |  | 0
Solar Water Heating System
A | Supply, install, and commission a 300-litre passive thermosiphon closed-circuit solar water heating system complete with a 300-litre horizontally mounted insulated storage tank with a 3 kW electric booster element, and 2 No. flat-plate solar heat collectors, each with a minimum area of 2m². The system shall be capable of delivering 300 litres of hot water at 60°C under typical Uganda solar conditions. It shall include all necessary piping connections, isolation valves, unions, thermal insulation (UV-resistant), mounting structures for roof installation, and all associated accessories to ensure a fully functional and safe system. The units shall be from a reputable manufacturer such as Solahart or equal and approved | No | 2 |  | 0
B | Cylindrical PVC vertical water tank 3000 Litres as Poly Tanks or equal approved complete with 25mm inlet ball valve, overflow, outlet and wash out and all accessories. | No | 2 |  | 0
C | Steel stand in standard section of 60x60x3mm thick, bracing 50x50x3mm thick ,8m high fixed in the ground next to the building complete with 2mm thick chequered plate, gard rails to height of 120mm high and all other accessories. | No | 2 |  | 0
D | 1/4" Mixer taps a single tap nozzle that runs both hot and cold, or a custom temperature combo. | No | 2 |  | 0
Wiring and lighting
A | Lighting points wired by 1.5mm2 copper cables in 25mm heavy guage PVC wall concealed conduit complete with MK boxes,1W1G switches and all accessories. | NO | 2 |  | 0
B | 6W LED Recessed Ceiling Panel Light Down Lights Surface Mount Flat 8 Inch Round | NO | 2 |  | 0
| TOTAL CARRIED TO COLLECTION |  |  |  | 0
5.1/6/6
COLLECTION
| Total carried forward from Page 5.1/1/1 |  |  |  | 0
| Total carried forward from Page 5.1/2/2 |  |  |  | 0
| Total carried forward from Page 5.1/3/3 |  |  |  | 0
| Total carried forward from Page 5.1/4/4 |  |  |  | 0
| Total carried forward from Page 5.1/5/5 |  |  |  | 0
| Total carried forward from Page 5.1/6/6 |  |  |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
5.1/7/7

## Bill 6.1 OXYGEN PIPING
PROPOSED OXYGEN PIPPING AND SUPPLY AT BUGEMBE HCIV JINJA DISTRICT
No | Description | Unit | Qty | Unit price VAT excl. (€) | Total price VAT excl. (€)
Element 1: Supply cable
1 | Semi Automatic manifold 2x3 | No. | 1 |  | 0
2 | Degreased Copper pipes 15mm | M | 100 |  | 0
3 | Fittings | Item | 1 |  | 0
4 | AVSU-1 Gas with Alarm | Item | 1 |  | 0
5 | Line Valve 15mm | No. | 2 |  | 0
6 | Three compartment trunking | M | 6 |  | 0
7 | Trunking 50x50 | M | 5 |  | 0
8 | End caps | No. | 10 |  | 0
9 | Oxygen Delivery outlet | No. | 12 |  | 0
10 | Flow Metre | No. | 12 |  | 0
11 | Fabrication | Item | 1 |  | 0
12 | Pig tail connectors | No. | 8 |  | 0
13 | 6.5 cubic meters cylinders | No. | 6 |  | 0
Total Element 1 excl. VAT |  |  |  |  | 0
Element 2: Concrete Platform
SUBSTRUCTURE (All Provisional)-3m x2.5m
Excavations
1 | Excavate oversite to remove top soil average 150mm deep and remove from site. | M3 | 1.5 |  | 0
2 | Excavate foundation trench not exceeding 1.50 m deep. | M3 | 2 |  | 0
3 | 150mm thick brickwork in cement sand mortar mix 1:4 as plith walling | SM | 30 |  | 0
4 | Remove excavated material from site | M3 | 1.5 |  | 0
5 | Return fill and ram selected excavated material around foundation | M3 | 1 |  | 0
6 | 1000 gauge polythene plastic sheeting with 300mm welted lap joints | Sq. | 7.5 |  | 0
Murram filling
7 | Murram filling well spread levelled rammed and consolidated in 100mm 'layers' | M3 | 1 |  | 0
Plain concrete class 15/20mm Aggregate in:
8 | 50 mm blinding under beams | M3 | 0.5 |  | 0
Vibrated reinforced Concrete Class 25/20mm
Aggregate in:
9 | 150 mm thick slab | M3 | 2 |  | 0
10 | Cement sand plaster 20mm thick to plinth walling mortar mix 1:3 | SM | 30 |  | 0
High Tensile Steel Bar Reinforcement
(Provisional)
11 | 12 mm | Kg | 60 |  | 0
12 | 8 mm | Kg | 8 |  | 0
13 | Fabric mesh reinforcement BRC mesh ref No. A142 laid in floor slab. | Sq. | 12 |  | 0
14 | Supply, fabricate and install 100mmx100mmx10mm steel angle frame with hold down hook bars 150mm placed at 300mm along the frame length and cast in concrete slab/beam complete with hole provision for securing the generator at installation | Lm | 9 |  | 0
Sawn Formwork as described to:
15 | Sides of ground beam and slab | Lm | 12 |  | 0
Total Element 2 excl. VAT |  |  |  |  | 0
Element 3: Shelter frame
PURPOSE MADE STANDARD Steel burglar proofing made from 20 x 20 x 2mm SHS vertical grills everywhere placed at 150mm along the shelter perimeter and 60 x 40x2mm vertical supports at 4 no corner points, 2no door support and 1no mid back side RHS : one coat red oxide primer as per Architect's detailed drawing
A | Cage; size 4200mm x 2700mm x 2400mm high front and 2100mm high on the back; complete with and including 1500 x 2100mm high steel grilled door | Item | 1 |  | 0
PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat and two Gloss finishing coats; on metal work : to
B | General steel surfaces | Item | 1 |  | 0
ROOF WORKS
Structural Steelwork
The rates for structural steel work should include all plates, stiffeners, bolts, welded joints, all connections and accessories; painting and decorations; as per the architect’s and structural engineer’s drawings; the contractor must study the drawings and ensure that his price includes all items as shown on the drawings
Structural Steelwork : framed : one coat red-oxide primer;
C | 50 x 50 x 2.0mm SHS wall plate for back and front of shelter | Kg | 50 |  | 0
D | 50 x 25 x 2.0mm SHS for rafter placed at side, middle and side | Kg | 45 |  | 0
E | 50 x 25 x 2.0mm SHS for Purlin placed at top, middle and bottom of roof structure | Kg | 50 |  | 0
SUNDRIES
F | Allow for all connections, plates, cleats, weld joints and heavy duty bolts, nuts and washers to approval, including all builders work during erection of shelter | Item | 1 |  | 0
ROOF COVERING
26 Gauge pre-painted IT4 roofing sheets : fixed to angle purlins with J-bolts : in
G | Sheet laid sloping not exceeding 22.5 degrees from horizontal overall roof cover size 3.5m x 3.0m. | SM | 20 |  | 0
H | Allow for supply and installation of all necessary safety and user signage | Item | 1 |  | 0
A | STEEL GRILLLLED DOOR detail see below;
PURPOSE MADE GRILLED DOORS: Standard Steel grilled door comprising of: 50 x 50 x 3mm RSA door frame; 40 x 40 x 3mm RHS framing and transoms; all iron-mongery and accessories; one coat red oxide primer; as per Architect's drawing
B | Door size 1500 x 2100mm high (overall) | No | 1 |  | 0
| PREPARE SURFACE AND APPLY ETCHING PRIMER; apply one coat primer, one undercoat and two Gloss finishing coats; on metal work surfaces | Item | 1 |  | 0
C | General door surfaces | Item | 1 |  | 0
Total Element 3 excl. VAT |  |  |  |  | 0
Grand total excl. VAT (€): |  |  |  |  | 0

## Bill 7.1 Solar Hot water system
B | SOLAR WATER HEATERS AND THE PLUMBING WORKS
Item | Description | Unit | Qty | Rate (Euro) | Amount (Euro)
A | Supply, install, and commission a 300-litre passive thermosiphon closed-circuit solar water heating system complete with a 300-litre horizontally mounted insulated storage tank with a 3 kW electric booster element, and 2 No. flat-plate solar heat collectors, each with a minimum area of 2m². The system shall be capable of delivering 300 litres of hot water at 60°C under typical Uganda solar conditions. It shall include all necessary piping connections, isolation valves, unions, thermal insulation (UV-resistant), mounting structures for roof installation, and all associated accessories to ensure a fully functional and safe system. The units shall be from a reputable manufacturer such as Solahart or equal and approved | No | 2 |  | 0
B | Cylindrical PVC vertical water tank 3000 Litres as Poly Tanks or equal approved complete with 25mm inlet ball valve, overflow, outlet and wash out and all accessories. | No | 2 |  | 0
C | Steel stand in standard section of 60x60x3mm thick, braching 50x50x3mm thick ,8m high fixed in the ground next to the building complete with 2mm thick chequered plate, gard rails to height of 120mm high and all other accessories. | No | 2 |  | 0
Plumbing
INTERNAL WATER SUPPLY AND DISTRIBUTION
All Cold and Hot Water piping shall be PPR pipe PN25 complete with Tees, Sockets, Elbows, Threaded adapters, Threaded elbows, Reducers and all associated fittings.
PIPE WORK
D | 32mm PPR cold water Pipe work complete. | m | 50 |  | 0
E | 25mm PPR cold water Pipe work complete. | m | 70 |  | 0
F | 20mm PPR cold water Pipe work complete. | m | 50 |  | 0
G | 32mm gate valves | No | 2 |  | 0
H | 25mm gate valves | No | 4 |  | 0
I | 20mm angle valves | No | 4 |  | 0
J | Flexible tube 450mm long complete | No | 4 |  | 0
K | Excavation for the distribution and supply pipes including back fill after laying of pipes; including excavation for column bases for the steel water tank. | Item | 1 |  | 0
L | 1/4" Mixer taps a single tap nozzle that runs both hot and cold, or a custom temperature combo. | No | 2 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0

## Mpumudde
Item | Description | Unit | Qty | Rate (Euro) | Amount (Euro)
A | AIR CONDITIONING INSTALLATION IN THE THEATRE
A.1 | Single Split Air Conditioning Unit LG or equal approved rated at 24,000 Btu/hr - R410a, Dual Inverter with an indoor wall mounted unit, outdoor unit, and remote control, complete with AVS 30A, CB 32A, DP switch, mounting brackets, 2.5 sq.mm power cable, copper pipes, armaflex, drainpipe, and all other installation assorted accessories. | Pcs | 2 |  | 0
B | RAINWATER HARVESTING
uPVC Key terrain fixed in accordance with manufacturer's instructions
B.1 | PVC gutters 127mm diameter complete with clips space at 600mm centers | LM | 280 |  | 0
B.2 | Extra over for stop ends/bends. | NO | 8 |  | 0
B.3 | Extra over for gutter straight connectors. | NO | 40 |  | 0
B.4 | Extra over gutter for outlet to suit 127mm diameter pipe. | NO | 16 |  | 0
B.5 | Extra over for bends | NO | 56 |  | 0
B.6 | Extra over for shoe. | NO | 40 |  | 0
B.7 | 110mm PN6 PCV pipe as down pipe | LM | 120 |  | 0
B.8 | Extra over for gutter coner connectors. | NO | 16 |  | 0
B.9 | Allow for drainage around the building | Item | 4 |  | 0
B.10 | Cylindrical PVC vertical water tank 10000 Litres as gentex or equal approved complete with all accessories for rain water harvesting. | NO | 4 |  | 0
B.11 | Platform in grade 20 concrete foundation measurering 2400mm diameter, 600mm high above ground tank base including builders' work. | NO | 4 |  | 0
B.12 | 110mm PN6 PVC pipe from Roof gutters to water tank | LM | 24 |  | 0
C | Fire Extinguishers
C.1 | Carbon Dioxide portable fire extinguisher 5kg as NAFFCO CO2 gas extinguisher Model NC5 or equal approved. | NO | 1 |  | 0
C.2 | Dry powder portable fire extinguisher 9 kg as NAFFCO ABC powder Model NP9 or equal approved. | NO | 1 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0